# Major non-compliance: waste-water treatment works (public and private)

Table 1: Major impact of the authorised activity

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Any authorisation condition. | Non-compliance causes or is likely to cause: - Category 1 or 2 environmental event. - Breach of water standard. - Significant and sustained adverse trend for groundwater. | - Environmental events guidance. - Relevant water standards. - Groundwater monitoring or modelling demonstrates, significant and sustained adverse trend. | Demonstration that the cause or likely cause of the harm has ceased or been resolved. This can include monitoring and modelling. |
| Descriptive conditions. No significant: - Iridescence / sheen; - Discolouration; - Deposition of solids; - Increased foaming; or - Microbiological growth in the receiving waters. | Non-compliance causes or is likely to cause a Category 1 or 2 environmental event. | - Site inspection. - Environmental events guidance. - Descriptive conditions guidance. | Demonstration that the cause or likely cause of the harm has ceased or has been resolved, and the visual impact is now compliant. |
| Single-tier numeric limits set to achieve environmental standards. | More than twice the limit specified in authorisation. Exceptions: - pH: limit exceeded by more than 1 unit. - Temperature: exceeded by more than 5oC. - Any breach of single tier bacterial limit. | Assess against authorisation limit using: - SEPA monitoring data. - Operator self-monitoring. - Regulatory Method (WAT-RM-40). Note: the suspected solids limit of 100 mg/l for primary treated sewage effluent falls into this category. | Major non-compliance remains until next compliant planned sample is compliant. Seasonal sampling – if a discharge is major non-compliant at the end of the season this will be lifted. |
| Two-tier numeric limits set to achieve environmental standards (set according to a specified statistical distribution). | - Any breach of upper-tier limit. - Number of planned samples exceeding lower tier limit is greater than the maximum number of permitted exceedances specified in the look up table (usually Appendix 1 in authorisation). - Exception: - A breach of the upper tier UWWTD limit where sample compliance is achieved by meeting the minimum percentage reduction of influent load. | Assess against authorisation conditions and permitted exceedances look up table: - SEPA monitoring data. - Operator self-monitoring. - Regulatory Method (WAT-RM-40). Note: the suspended solids limit of 100 mg/l is effectively an upper tier limit for secondary / tertiary treated sewage effluent discharges. | - Upper tier: when the next planned sample result is compliant. - Lower tier: when number of planned samples exceeding lower tier limit is less than the maximum number of permitted exceedances in the previous 12 months - specified in the look up table - Seasonal sampling – if a discharge is major non-compliant at the end of the season this will be lifted. |
| Annual numerical limits. | Any breach of the limit specified in the authorisation. Exception: A breach of the annual mean UWWTD limit where sample compliance is achieved by meeting the minimum percentage reduction of influent load. | Assess against limit in authorisation e.g. - Annual mean limits for iron or aluminium in samples taken over a 12-month rolling period. - UWWTD annual mean limits for phosphorus or nitrogen (in composite samples taken over a calendar year), taking into account, where appropriate, percentage reduction in influent loading. Using: - SEPA monitoring data. - Operator monitoring data. - Regulatory Method (WAT-RM-40). | - For limits based on a rolling 12-month period, the major non-compliance will apply from the date of the breach until the point when data from the previous 12 months does not exceed the authorisation limit. - For limits based on a calendar year, major non-compliance will apply from the date of the breach until the end of the relevant calendar year. |

Table 2: Scope of site

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Discharge points for final effluent or spills from combined sewer overflows, settled storm sewage overflows or emergency overflows: location and design. | Discharge points not as specified in authorisation (e.g. different waterbody) and/or Diffuser(s) or outfall location not achieving acceptable dispersion as assessed by visual assessment and/or investigative monitoring. | - Site inspection - NGR check. - SEPA investigative monitoring data. | Evidence that the discharge point is at the authorised location. |
| Screens. | Screens required by authorisation are: - Not installed OR - Maceration or comminution is used to achieve screening standards. | - Site inspection. - Environmental events guidance. Note: If the screen is present but not operating, it should be assessed under Table 4 (management of site). | Evidence that screens have been installed and are operating or that maceration / comminution plant has been decommissioned. |
| Dry Weather Flow (DWF) limits. | Exceeds the authorised limit for three consecutive years. OR problems with flow data (more than 108 days data missing in a 365-day period). | - Assess annual data return using document CAS-G-004 Flow recording and reporting at sewage treatment works and on the sewer network for guidance on actions required by operator. - Assessment of a compliance recovery plan submitted by operator. | Major non-compliance will apply from date of breach (after 3 years of non-compliance with DWF figures) until evidence demonstrates that the site complies with DWF limit or, where appropriate, authorisation is varied. |
| Overflow settings for combined sewer overflow and settled storm sewage overflows. | Overflows operating: - In the absence of rainfall or snowmelt and / or - Before the authorised pass forward flow has been exceeded. Note: in the absence of rainfall means five days without significant rainfall in the catchment. | - Annual data returns (maximum pass forward flow data). - Site inspection. - Records review. - Operator incident report (e.g. EPI notification). | Report provided that identifies the cause, actions taken and demonstrates compliance, this should include spill event, rainfall and flow data (where available) that can be easily cross referenced to demonstrate compliance. |
| Overflow settings for emergency overflows. | Overflow operating, not due to: - Power failure or - Rising main failure or - Blockage of downstream sewer. | - Site inspection. - Operator incident report (e.g. EPI notification). | Report provided that identifies the cause, actions taken and demonstrates compliance, this should include spill event data. |
| Provision of sewage storage facility (storm tanks and / or pumping stations) where required by the authorisation. | Sewage storage facilities (storm tanks and pumping stations): - Are not installed or not of the size required by the authorisation or - Are full of gassing, septic material (not being emptied in a timely fashion) or - Contain levels of grit that reduce the capacity for functional storm sewage storage to less than 75% of the authorisation requirement. | - Site inspection. | Evidence that sewage storage is in place and providing the capacity required by authorisation e.g. after cleaning, removal of debris etc |
| Sewage treatment system (where specified in authorisation). | Treatment system specified in authorisation is not installed. | - Site inspection. - Environmental event investigation. Note: mostly relevant to private sewage treatment systems. | Evidence that demonstrates treatment plant is as specified in the authorisation. |

Table 3: Understanding of authorised activities

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Requirement to report incidents (either in operation of plant or environmental events). | - Unless specified otherwise in the authorisation, failure to notify SEPA within 24 hours of an event that has caused or could cause an adverse impact upon the environment or human health. - Failure to provide an incident report requested by SEPA within 14 days of the incident (or an agreed date) or the report does not comply with the information requirements specified in the authorisation. | - Operator notification received within timescale (by phone call or email). - Operator incident report submitted in accordance with authorisation conditions. - Operator incident report (e.g. EPI notification). “incident” means any of the following situations: - Accidents, malfunction, breakdown, or failure of plant or techniques. - Or any event such as force majeure or emergency actions, that results or is likely to result, in a breach of any condition of the authorisation. | The operator has notified SEPA of the incident / event and has provided a report of adequate quality. |
| Requirement to submit records, reports or data. | - Failure to make a data return (including nil returns) and / or records or reports required by the authorisation, that are of adequate quality within 30 days of the required submission date. | Annual data return assessments (where required by the authorisation) including: - Dry weather flow figure. - Overflow spill data. - Mean daily flow figure. - Maximum rate of flow of sewage that passes overflow weirs. Other reports required by the authorisation including: - Increase or introduction of hazardous substances (List I or II substances) in the influent sewage stream. Note: If the data return contains a figure for a parameter that is likely to be incorrect (e.g. the dry weather flow figure if more than 108 days of influent flow data are missing), this will be recorded as major non-compliance under maintenance of measuring equipment condition. Notification of malfunction of measuring or monitoring equipment will be assessed under notification of incidents. | - Required data submission. - Or if no data available, MNC will be resolved on receipt of an information submission that includes: - Corrective actions and reasons for missing information. - Assessment of the likely impact from missing data. - Evidence that the records are now being recorded and kept. - SEPA will assess submission and ascertain if enough information is provided to resolve compliance. |
| Requirement to carry out monitoring and submit routine monitoring data (only refers to those operators subject to the Operator Self Monitoring (OSM) scheme). | - Failure to undertake sampling in accordance with agreed survey schedule, or - Significant deviation from requirements set out in MACS-WAT-01: Sampling and chemical testing of water, or - Significant deviation from requirements set out in MACS-WAT-02: Sample and data management. | - Assess OSM data provided by operator. - UWWTD discharge determinands where any result shortfall for BOD, COD, Total P or Total N. - All CAR discharge determinands where more than 10% shortfall in results received. Excluding: - ‘influent samples’ that are optional. - ‘weather’ (as defined in UWWTD). - Observations and / or investigative samples. | Evidence that demonstrates full investigation carried out and corrective action implemented in accordance with MACS-TG-03 Dealing with non-conformance. |
| Provision of flow monitoring, event recording equipment, telemetry, autosamplers. | Items required by authorisation and by WAT-G-065 EASR Guidance: Permit Activity: Municipal Sewage Treatment Works, not installed: - Monitoring equipment (e.g. flow meters, event recorders) or facilities or - Telemetry or - Final effluent autosamplers. | - Site inspection. - Assessment of operator data. Note: failure to provide inlet autosampler is ‘Non-compliance’, not ‘Major non-compliance’. | Evidence that plant is installed and operating as it should, this should include photographs and data output from the equipment. |
| Provision of suitable sampling locations. | Sampling location required by authorisation not provided or failure to provide a representative sample. | Site inspection. | Evidence that sample point is installed and / or providing a representative sample. |
| Requirement to keep records. | - Failure to provide, upon request, information required by the authorisation. - Information submitted is not true and accurate. - Records are not kept for the minimum duration specified in the authorisation. | - Site inspection. - Desk-based inspection. - Incident investigation. | - Required data submission. - Or if no data available, MNC will be resolved on receipt of an information submission that includes: - Corrective actions and reasons for missing information. - Assessment of the likely impact from missing data. - Evidence that the records are now being recorded and kept. - SEPA will assess submission and ascertain if enough information is provided to resolve MNC. |

Table 4: Overall management of authorised activities

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Compliance with authorisation conditions. | - Multiple non-compliance (same or different conditions) that cumulatively equate to major non-compliance. - The major non-compliance will be recorded against the condition that places the responsibility on the Authorised Person to ensure compliance with the conditions of the authorisation. | Having regard to condition-specific guidance where this exists and / or environmental events guidance and events records. - Greater than or equal to four Category 3 events within a 365-day period that have been caused by a breach of the same condition. - Unless otherwise stated within the site authorisation, multiple non-compliance breaches may be considered collectively as major non-compliance depending on the particular circumstances. SEPA's assessment will be subject to additional governance checks to ensure national consistency in decision-making. | Demonstration that the cause or likely cause of the harm has ceased or been resolved. This can include monitoring and modelling. |
| Conditions covering management of site, activity infrastructure. | Plant / infrastructure: - Frequent breakdown of critical plant with minor unauthorised releases; OR - Infrequent or frequent breakdown of any plant (critical and non-critical) that leads to, or may lead to, a significant breach of numeric limits (verified by investigative not routine sampling). | - Site inspection. - Communications with operator. - Operator notifications (EPIs). - SEPA investigative monitoring data. | Evidence that the problem is resolved and / or plant is operating as it should. |
| Operation and calibration of measuring and monitoring equipment (flow meters, event recorders, autosamplers, telemetry etc). | - Installed equipment (if required by authorisation and WAT-G-065 wat-g-065_permit_guide_municipal_sewage_treatment-_works.docx) not working as required (or accurately) for extended periods of time, for example: - Breakdowns of inlet flow meter(s) exceed 108 days in 12 months. - Breakdowns of event recorders and flow meters at overflows exceed 30 days in 12 months. - No calibration checks of flow meters and / or event recorders performed in accordance with authorisation requirements. - Required telemetry is not operating. - Final effluent autosamplers are not operating according to the authorisation conditions e.g. not at correct temperature. | - Assessment of data returns. - Site inspection. - SEPA request for data and calibration records. - Incident notifications (EPIs). - Calibration of flow meters, use CAS-G-002: Calibration of monitoring and measurement equipment at sewage treatment works (CAS-G-002). | Evidence that the equipment issue has been resolved and is operating as it should, including evidence of calibration checks where appropriate. |

Table 5: Wider legal environmental requirements and financial non-compliance

EPAS is designed to provide a more accurate picture of legal environmental compliance. Under EPAS we will therefore assess compliance of the following situations as it is important a performance rating reflects this.

| Contravention | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Undertaking a regulated activity without authorisation. | Undertaking a regulated activity without authorisation, for example: - Use of chlorination to achieve disinfection, contrary to authorisation condition. - Chemical dosing to achieve discharge standards. | Site inspection. | Unauthorised activity ceases, and, where appropriate, authorisation is varied to include the activity or appropriate authorisation obtained. |
| Environmental event at an authorised site that is unrelated to the authorised activity. | Causes a: - Category 1 or 2 environmental event. - Breach of water or air quality standard. - Significant and sustained adverse trend for groundwater. Examples: oil spill or sludge spill from a WWTW. | - Environmental events guidance. - Groundwater monitoring, investigation or modelling demonstrates significant and sustained adverse trend. | Demonstration that the cause or likely cause of the harm has ceased or been resolved. This can include monitoring and modelling. |
| Non-payment of annual charges. | Escalation to debt collection or if debt goes into the next financial year. (Non-compliance is when payment is more than 90 days late.) | Monthly debtors report. | Payment of annual charges. (Payment plan agreed with SEPA is equivalent to a compliance recovery plan.) |

For information on accessing this document in an alternative format or language, please contact SEPA by email or telephone 0300 099 6699.

If you are a user of British Sign Language (BSL), the Contact Scotland BSL service gives you access to an online interpreter, enabling you to communicate with us using sign language.

<Report date here (month, year)>

Adequate quality means containing the required information to enable the assessment of compliance with authorisation conditions.

“critical plant” is defined as those parts of a treatment system that have a significant and immediate role in ensuring discharge effluent quality standards and whose failure is difficult to mitigate without there being a significant effect on effluent quality (e.g. biological treatment stage, final settlement stage, screens on combined sewer overflows, settled storm sewage overflows and emergency overflows, storm tank return systems, disinfection treatment). They will be a significant part of the treatment system and / or close to the end of the treatment chain.