

SEPA Guidance:

Version 3.0: August 2025

IND-LF-G-009

Monitoring of landfill leachate, groundwater and surface water

This document has been modified from the Environment Agency document ‘Guidance on Monitoring of Landfill Leachate Groundwater and Surface Water, January 2001’. SEPA gratefully acknowledge the use of the Environment Agency document used to produce this Scottish Edition of the guide. It is only applicable to landfill sites in Scotland and should not be applied to landfills in England and Wales.

### Statement of Use

This report provides guidance on best practice for monitoring of landfill leachate, groundwater and surface water at licensed/permitted landfill sites. It is provided as guidance for SEPA staff, landfill operators and practitioners. The principles in this document will also be of value to new landfill developments that require monitoring as part of an environmental assessment for planning purposes. Some of the principles will have relevance for monitoring of landfill sites which are closed and unlicensed.

#### Research Contractor & Environment Agency’s Project Manager

This document has been modified from one produced under Environment Agency R&D project HOCO\_232 by a team of Independent Consultants led by Peter Dumble and Charles Ruxton (joint principal authors). Additional input and debate on statistical / chemometric issues for the project was provided by John Thompson. Ellen Pisolkar who contributed to sections on surface water monitoring. Other material throughout the document was provided by numerous sources within the Environment Agency. Diagrams were prepared by Max Fuller of Peter Dumble Associates.

Peer review on work in progress was carried out on behalf of Peter Dumble Associates by Steve Bennett.

Contract administration and collation of all written material was co-ordinated by Peter Dumble Associates.

The Environment Agency’s Project Managers for R&D Project HOCO\_232 were:

Mr. Paul Wright - Environment Agency, Anglian Region Dr Louise de Rome - ETSU, AEA Harwell.

# Contents

[Part 1: Context & Principles 10](#_Toc193890933)

[1. Introduction 10](#_Toc193890934)

[1.1 Landfill leachate and its impact 10](#_Toc193890935)

[1.2 Reasons for monitoring 10](#_Toc193890936)

[1.3 The need for reliable long-term monitoring records 11](#_Toc193890937)

[1.4 Aims of guidance 12](#_Toc193890938)

[1.5 Use of guidance 12](#_Toc193890939)

[1.6 Legislation, policy and responsibilities 13](#_Toc193890940)

[1.7 Structure of documentation 13](#_Toc193890941)

[2. Landfills, Leachate and its Effect on Surrounding Waters 15](#_Toc193890942)

[2.1 Introduction 15](#_Toc193890943)

[2.2 Waste types, landfill design and leachate 16](#_Toc193890944)

[2.3 Waste types, landfill design and leachate 20](#_Toc193890945)

[2.4 Effects of leachate on receptors 23](#_Toc193890946)

[3. Monitoring Principles 25](#_Toc193890947)

[3.1 Introduction 25](#_Toc193890948)

[3.2 Purpose and context of monitoring 25](#_Toc193890949)

[3.3 Quality assurance 27](#_Toc193890950)

[3.4 Monitoring in relation to risk 28](#_Toc193890951)

[3.5 Statistical aspects of monitoring 29](#_Toc193890952)

[3.6 Introduction 35](#_Toc193890953)

[3.7 The Site Control and Monitoring Plan 40](#_Toc193890954)

[4. Risk-Based Monitoring 41](#_Toc193890955)

[4.1 Introduction 41](#_Toc193890956)

[4.2 The Risk-Assessment Process 42](#_Toc193890957)

[4.3 Documentation to Accompany the Design of a Risk-Based Monitoring Programme 44](#_Toc193890958)

[Part 2: The Site Control and Monitoring Plan 55](#_Toc193890959)

[5. Design Issues and Monitoring Objectives 55](#_Toc193890960)

[5.1 Introduction 55](#_Toc193890961)

[5.2 Introduction 56](#_Toc193890962)

[5.3 Management and technical competence 57](#_Toc193890963)

[5.4 Monitoring objectives 58](#_Toc193890964)

[6. Monitoring Locations and Schedules 69](#_Toc193890965)

[6.1 Introduction 69](#_Toc193890966)

[6.2 The number and location of monitoring points 69](#_Toc193890967)

[6.3 Introduction 77](#_Toc193890968)

[6.4 Specification of monitoring schedules 90](#_Toc193890969)

[7. Assessment Criteria and Contingency Actions 109](#_Toc193890970)

[7.1 Introduction 109](#_Toc193890971)

[7.2 Compliance and assessment 109](#_Toc193890972)

[7.3 Assessment criteria 110](#_Toc193890973)

[7.4 Contingency actions 116](#_Toc193890974)

[8. Design of Monitoring Points 126](#_Toc193890975)

[8.1 Introduction 126](#_Toc193890976)

[8.2 General design issues 126](#_Toc193890977)

[8.3 Identification and accessibility of monitoring points 129](#_Toc193890978)

[8.4 Leachate monitoring points 132](#_Toc193890979)

[8.5 Groundwater monitoring points 139](#_Toc193890980)

[8.6 Surface water monitoring points 146](#_Toc193890981)

[9. Monitoring Methodology 149](#_Toc193890982)

[9.1 Introduction 149](#_Toc193890983)

[9.2 Objectives of monitoring methodology 149](#_Toc193890984)

[9.3 Safety of monitoring personnel 151](#_Toc193890985)

[9.4 Specification of monitoring protocols 152](#_Toc193890986)

[9.5 Physical monitoring measurements 154](#_Toc193890987)

[9.6 Collecting an appropriate water quality sample 159](#_Toc193890988)

[9.7 Collecting a sample of surface water 163](#_Toc193890989)

[9.8 Unsaturated zone sampling 164](#_Toc193890990)

[9.9 Purging and sampling of monitoring points 165](#_Toc193890991)

[9.10 Field measurements of water quality 172](#_Toc193890992)

[9.11 Preparation and handling of water samples for laboratory analysis 174](#_Toc193890993)

[9.12 Laboratory analyses 179](#_Toc193890994)

[9.13 Quality control sampling 181](#_Toc193890995)

[9.14 Documentation 186](#_Toc193890996)

[10. Monitoring Locations and Schedules 188](#_Toc193890997)

[10.1 Introduction 188](#_Toc193890998)

[10.2 Data management principles 188](#_Toc193890999)

[10.3 Quality assurance 189](#_Toc193891000)

[10.4 Data collection 190](#_Toc193891001)

[10.5 Collation of monitoring data and preliminary storage 191](#_Toc193891002)

[10.6 Data validation 192](#_Toc193891003)

[10.7 Storage and archiving of validated data 194](#_Toc193891004)

[10.8 Data presentation, review and interpretation 195](#_Toc193891005)

[10.9 Reporting 198](#_Toc193891006)

[Selected Bibliography 206](#_Toc193891007)

[Glossary 206](#_Toc193891008)

[Chapter 1: Introduction 206](#_Toc193891009)

[Chapter 2: Landfills, Leachate and its Effect on Surrounding Waters 208](#_Toc193891010)

[Chapter 3: Monitoring Principles 212](#_Toc193891011)

[Chapter 4: Risk-Based Monitoring 213](#_Toc193891012)

[Chapter 5: Design Issues and Monitoring Objectives 213](#_Toc193891013)

[Chapter 6: Monitoring Locations and Schedules 214](#_Toc193891014)

[Chapter 7: Assessment Criteria and Contingency Planning 215](#_Toc193891015)

[Chapter 8: Design of Monitoring Points 215](#_Toc193891016)

[Chapter 9: Monitoring Methodology 218](#_Toc193891017)

[Chapter 10: Data Management and Reporting 223](#_Toc193891018)

[Appendix 1: Example Monitoring Point Construction Forms and Registers 226](#_Toc193891019)

[A1.1 Monitoring point construction record sheet for wells and boreholes 226](#_Toc193891020)

[A1.2 Monitoring point surveying and monitoring history record sheet for wells and boreholes 243](#_Toc193891021)

[A1.3 Monitoring point register for wells and boreholes 250](#_Toc193891022)

[A1.4 Monitoring point register for surface waters and springs 254](#_Toc193891023)

[Appendix 2: Datum Point Identification and Measurement 260](#_Toc193891024)

[A2.1 Introduction 260](#_Toc193891025)

[A2.2 Surface water datum points 260](#_Toc193891026)

[A2.3 Datum points for built leachate monitoring points 260](#_Toc193891027)

[A2.4 Datum points for groundwater monitoring points 262](#_Toc193891028)

[Appendix 3: Leachate Monitoring Points Built During Landfilling 263](#_Toc193891029)

[A3.1 Types of built leachate monitoring points 263](#_Toc193891030)

[A3.2 CQA and monitoring objectives 263](#_Toc193891031)

[A3.3 Construction design features 264](#_Toc193891032)

[A3.4 Foundations 264](#_Toc193891033)

[A3.5 Structure 265](#_Toc193891034)

[A3.6 Means of leachate entry 267](#_Toc193891035)

[A3.7 Headworks design considerations 268](#_Toc193891036)

[Appendix 4: Borehole Drilling Methods 269](#_Toc193891037)

[A4.1 Introduction 269](#_Toc193891038)

[A4.2 Design issues 269](#_Toc193891039)

[A4.3 Drilling methods 273](#_Toc193891040)

[A4.4 Sources of contamination 279](#_Toc193891041)

[References 280](#_Toc193891042)

[Appendix 5: Borehole Completion Details 281](#_Toc193891043)

[A5.1 Introduction 281](#_Toc193891044)

[A5.2 Design considerations 281](#_Toc193891045)

[A5.3 Lining materials and screens 283](#_Toc193891046)

[A5.4 Annular backfill 285](#_Toc193891047)

[A5.5 Multi-level monitoring installations 287](#_Toc193891048)

[A5.6 Headworks 290](#_Toc193891049)

[References 291](#_Toc193891050)

[Appendix 6: Borehole Cleaning and Development 293](#_Toc193891051)

[A6.1 Introduction 293](#_Toc193891052)

[A6.2 Factors affecting borehole development 293](#_Toc193891053)

[A6.3 Methods for borehole development 294](#_Toc193891054)

[A6.4 Development in low permeability formations 298](#_Toc193891055)

[References 299](#_Toc193891056)

[Appendix 7: Borehole Inspection and Maintenance 300](#_Toc193891057)

[A7.1 Introduction 300](#_Toc193891058)

[A7.2 Factors causing borehole deterioration 300](#_Toc193891059)

[A7.3 Checks on borehole performance 302](#_Toc193891060)

[A7.4 Investigative techniques 304](#_Toc193891061)

[A7.5 Maintenance and rehabilitation of boreholes 309](#_Toc193891062)

[References 311](#_Toc193891063)

[Appendix 8: Example Monitoring Record Forms 312](#_Toc193891064)

[A8.1 Introduction 312](#_Toc193891065)

[A8.2 Environmental observation record form 312](#_Toc193891066)

[A8.3 Water movements record form 318](#_Toc193891067)

[A8.4 Equipment calibration forms 325](#_Toc193891068)

[A8.5 Water level record form 334](#_Toc193891069)

[A8.6 Borehole purging record 341](#_Toc193891070)

[A8.7 Sample collection form 355](#_Toc193891071)

[A8.8 Laboratory analysis request form 369](#_Toc193891072)

[A8.9 Chain of custody document 369](#_Toc193891073)

[Appendix 9: Example Monitoring Protocols 377](#_Toc193891074)

[A9.1 Introduction 377](#_Toc193891075)

[A9.2 Structure of monitoring protocols 377](#_Toc193891076)

[A9.3 Example protocol for sampling groundwater or leachate from a monitoring borehole by pumping 379](#_Toc193891077)

[A9.4 Example protocol for decontamination of equipment 396](#_Toc193891078)

[References 399](#_Toc193891079)

[Appendix 10: Sampling Equipment 400](#_Toc193891080)

[A10.1 Introduction 400](#_Toc193891081)

[A10.2 Level measurement equipment 400](#_Toc193891082)

[A10.3 Borehole sampling equipment 402](#_Toc193891083)

[A10.4 Surface water sampling equipment 411](#_Toc193891084)

[A10.5 Unsaturated zone sampling equipment 412](#_Toc193891085)

[References 414](#_Toc193891086)

[Appendix 11: Quality Control Sampling 417](#_Toc193891087)

[A11.1 Introduction 417](#_Toc193891088)

[A11.3 Processing of QC samples and data 420](#_Toc193891089)

[Appendix 12: Laboratory Analysis 422](#_Toc193891090)

[A12.1 Preamble 422](#_Toc193891091)

[A12.2 Sample handling and preparation 422](#_Toc193891092)

[A12.3 Specification of analytical methods 422](#_Toc193891093)

[A12.4 Laboratory quality control 428](#_Toc193891094)

[A12.5 Laboratory reporting 429](#_Toc193891095)

[Appendix 13: Data Validation 431](#_Toc193891096)

[A13.1 Introduction 431](#_Toc193891097)

[A13.2 Monitoring data 432](#_Toc193891098)

[A13.3 Data validation 433](#_Toc193891099)

[A13.4 Validation of water level and flow data 434](#_Toc193891100)

[A13.5 Validation of water chemistry data 435](#_Toc193891101)

[A13.6 Validation of biological data 444](#_Toc193891102)

[A13.7 Automation of data validation 444](#_Toc193891103)

[References 444](#_Toc193891104)

[Glossary 446](#_Toc193891105)

If you would like this document in an accessible format, such as large print, audio recording or braille, please contact SEPA by emailing [equalities@sepa.org.uk](mailto:equalities@sepa.org.uk)

**This guidance has been updated to meet accessibility standards and to replace certain references to legislation with references to the Environmental Authorisations (Scotland) Regulations 2018. It has not been reviewed beyond this. We are aware that sections of this guidance may need to be updated, and this work will be completed in due course.**

# Part 1: Context & Principles

# Introduction

## Landfill leachate and its impact

Landfill leachate is a potentially polluting liquid, which unless returned to the environment in a carefully controlled manner may cause harmful effects on the groundwater and surface water surrounding a landfill site.

For example, leachate from a biodegradable landfill will contain significant concentrations of substances such as ammoniacal-nitrogen, which is toxic to many organisms or run-off arising from a landfill containing only soil and rubble may contain suspended solids, be turbid and threaten fish and other aquatic organisms.

## Reasons for monitoring

An Environmental Authorisations (Scotland) Regulations (“EASR”) permit will contain conditions to provide assurance that the landfill operation does not cause harm to human health or the environment. This will normally include a requirement for a monitoring programme.

There are many types of monitoring which may be undertaken at landfill sites however, this guidance only relates to the monitoring of groundwater, surface water and leachate at landfill sites. Specific reasons for monitoring are:

* To meet the requirements of legislation, such as the Environmental Authorisations (Scotland) Regulations 2018 and the Groundwater Regulations 1998.
* To demonstrate that the landfill is performing as designed.
* To provide reassurance that leachate controls are preventing pollution of the environment (by reference to a pre-established baseline).
* To indicate where further investigation is required and, where risks are unacceptable, the need for measures to prevent, reduce or remove pollution by leachate and
* To identify when a site no longer presents a significant risk of pollution or harm to human health (to enable an application for a certificate of completion to be made, thereby formally ending the licensing process and the legal duty to monitor).

## The need for reliable long-term monitoring records

Monitoring is a long-term commitment accompanying the development, operation and post closure management of all landfill sites. Landfill sites containing biodegradable or other polluting wastes may need to be monitored for periods of up to 50 years or more after completion of landfilling. To ensure consistency and long-term reliability of monitoring records, monitoring programmes should be:

* Targeted and risk-based to answer specific questions required for licence or permit compliance and to provide more detailed information where specific risks are identified.
* Balanced against minimum statutory requirements.
* Undertaken by competent personnel.
* Robust and fit for the purpose for which they are designed, with proper regard to quality assurance and quality control and
* presented and interpreted clearly and appropriately so that results can be reviewed by specialists and understood by non-specialists. Results should be in a form suitable for placing on a public register.

## Aims of guidance

The principal aims of this guidance document are:

* To provide technical guidance for monitoring of leachate, groundwater and surface water for EASR purposes and to comply with the Landfill Regulations.
* To describe how risk assessment principles should be used to design monitoring programmes and focus monitoring effort.
* To provide guidance for Scotland which conforms with the monitoring requirements of the EC Dangerous Substances Directive, EC Groundwater Directive and the European Union (EU) Landfill Directive and
* To provide monitoring guidance within the context of an overall catchment-based water protection strategy (EU Water Framework Directive).

## Use of guidance

This guidance will be used by SEPA as a primary reference source for drafting EASR permit conditions but can also be used by operators when preparing EASR authorisation applications or planning applications. As such this guidance can be applied to both new and existing landfills. The monitoring principles may also have some value for sites which are closed or unlicensed.

As with all technical guidance, issues are addressed which are the subject of ongoing research and development and which may be influenced by future legislation or policy. Where research and development is published to support alternative methodologies, or where experimental field data are produced to the same ends, these should always be given proper consideration. This guidance is intended as a basis for ensuring that issues are addressed in proportion to risk. **Every site is different and the development of permit conditions and monitoring requirements should not slavishly follow every detail in this guidance. The document contains many examples. These are to be treated as such and not used prescriptively**.

## Legislation, policy and responsibilities

In Scotland Landfills are regulated by the Environmental Authorisations (Scotland) Regulations 2018. These regulations require that the landfills comply with the Groundwater Directive. In this respect landfill sites should be subject to ‘requisite surveillance’.

The Landfill Directive 1999 is implemented in Scotland through the Landfill (Scotland) Regulations 2003 and EASR. The Directive requires that a control and monitoring programme be carried out and that control and trigger levels be established for groundwater. The Directive also sets out other monitoring requirements for leachate, groundwater and surface water (Annex III).

## Structure of documentation

This guidance provides an overview of key issues relevant to the management and implementation of leachate, groundwater and surface water monitoring programmes at licensed landfill sites. Its main aim is to provide sufficient information to understand the purpose of monitoring programmes and the main elements of work required for EASR permitting. It is divided into two parts as follows:

**PART 1: Context and Principals (Chapters 1 to 4)**

**Introduction** (Chapters 1 and 2).

Sets out the aims and content of guidance and provides a brief review of the characteristics and origin of landfill leachate and how leachate can give rise to pollution of water.

**Monitoring principles** (Chapter 3).

Outlines the principles underpinning the development of landfill monitoring guidance.

**Risk-Based Monitoring** (Chapter 4).

Describes how risks to groundwater and surface water receptors from landfill leachate should be evaluated to help define the aims of monitoring programmes and focus monitoring effort.

**PART 2: The Site Monitoring Plan (Chapters 5 to 10)**

**Design issues and monitoring schedules** (Chapters 5 and 6).

Describes the objectives and the issues to be addressed in designing a monitoring programme based on an evaluation of risks. Examples of monitoring schedules for high or low risk settings are presented.

**Assessment criteria** (Chapter 7).

Describes the means by which monitoring results are assessed against agreed criteria, and how assessment investigations and contingency measures can be triggered.

**Design of monitoring points and monitoring methodology** (Chapters 8 and 9).

Describes some of the practical issues associated with the design of monitoring points and the process of obtaining appropriate measurements and samples.

**Data management and reporting** (Chapter 10).

Describes the process of managing and reporting monitoring data with examples of reporting schedules and data presentation.

A series of supporting technical appendices is provided incorporating standard forms and additional supporting information on the design, construction and maintenance of monitoring points and monitoring methodology.

# Landfills, Leachate and its Effect on Surrounding Waters

## Introduction

Every landfill site is unique in its setting in relation to surrounding groundwater and surface water. Monitoring programmes should therefore be tailored to match site-specific conditions and to reflect an understanding of the design philosophy and engineering controls.

Risk assessment is based on the development of a site conceptual model which aids identification of source-pathway-receptor relationships. The vulnerability of individual receptors is evaluated against the hazard posed by a source (i.e. landfill leachate) and whether or not there are any migration pathways which can allow contaminants to migrate from the source to the receptor.

Harmful substances contained within a waste body represent the hazard or source of risk to groundwater and surface water receptors. This source is defined by:

* The amount of each substance present in the waste.
* The nature of each substance and the effects associated with it (e.g. toxicity).
* The mobility of each of these substances in the waste body and in water and
* The flow of water into and out of the waste body, controlled principally by the degree of containment offered by the landfill design and its geological setting.

The degree to which the source poses a risk depends on the presence of:

* A means of transport for the contaminants derived from the landfill (i.e. pathways) and
* Groundwater, abstractions or ecological systems, which could be affected by the contaminants (i.e. receptors).

It is important to realise that groundwater and surface water are both pathways and receptors.

The design of monitoring programmes should be based on the source-pathway-receptor linkage. This requires an understanding of waste, landfill engineering, the nature of the surrounding hydrogeological environment and the nature of surrounding surface water. It is the task of those responsible for designing the monitoring programme to gain this understanding. In cases of uncertainty, a precautionary approach should always be followed until the uncertainty has been resolved.

This chapter gives an overview of the technical issues underpinning the evaluation of risk to receptors from landfill leachate under the following headings:

* Section 2.2 waste types, landfill design and leachate (the source term).
* Section 2.3 ground and surface water flow (as pathways and receptors) and
* Section 2.4 effects of leachate on water receptors.

## Waste types, landfill design and leachate

### Waste Types

The Landfill Directive categorises landfills into:

* Hazardous.
* Non-hazardous and
* Inert.

However, historically prior to the implementation of the Landfill Directive, the nature of landfills has been more variable than this classification.

With regards to the monitoring of leachate, groundwater and surface water Regulation 16 of the Landfill (Scotland) Regulations 2003 requires that the monitoring measures in Schedule 4 should be complied with for all landfill types.

### Leachate formation

Leaching occurs when soluble components are dissolved (leached) out of a solid material by percolating water. Leachate may also carry insoluble liquids (such as oils) and small particles in the form of suspended solids. Depending on the waste types, further contaminants may be introduced as a result of biodegradation of wastes.

Almost any material will produce leachate if water is allowed to percolate through it. The quality of leachate is determined primarily by the composition and solubility of the waste constituents. If waste is changing in composition (For example, due to weathering or biodegradation), then leachate quality will change with time. This is particularly the case in landfills containing municipal waste. The stages in the generation of leachate set out below are representative of landfills that have received non-hazardous municipal waste:

* Leachate produced in the early stages of decomposition of waste is typically generated under aerobic conditions producing a complex solution with near neutral pH. This stage generally only lasts a few days or weeks and is relatively unimportant in terms of leachate quality. However because aerobic degradation produces heat, leachate temperatures can rise, sometimes as high as 80-90OC, and if this heat is retained it can enhance the later stages of leachate production.
* As decomposition processes develop, waste becomes anaerobic. At the early anaerobic stage (the acidogenic / acetogenic phase), leachate develops high concentrations of soluble degradable organic compounds and a slightly to strongly acidic pH. Ammonium and metal concentrations also rise during this phase. Even small quantities of this high-strength leachate can cause serious damage to surface water receptors.
* After several months or years, methanogenic conditions are established, and leachate becomes neutral or slightly alkaline, of lower overall concentration but still containing significant quantities of some pollutants (e.g. ammonium) and
* As biodegradation nears completion, aerobic conditions may return, and leachate will eventually cease to be hazardous to the environment.

It is critical to landfill risk assessment and monitoring that the composition of the landfill leachate is characterised. Wherever possible this should be based on site-specific sampling. It should be noted that the Landfill Directive will result in a change to the waste which is landfilled which is likely to have an impact on the quality of landfill leachates.

### Landfill hydrology

Leachate within the body of a landfill site is rarely static. Water enters the landfill principally as rainfall infiltrating from the surface. Any resulting leachate, which is not contained and managed within the site, could seep through the base or sides of the site or overspill to the surface. Leachate may also be pumped out of the site for treatment, disposal or recirculation. An awareness of the overall “water balance” is needed to design an effective monitoring programme. The water balance can be summarised by the following simplified equation:

L = total liquid inputs – total liquid outputs

Where: L is the amount of liquid contained in storage within the waste.

The leachate stored in the waste is not fully available to drain to the base of the site. Some is absorbed by the waste, and some may remain ‘perched’ above low permeability layers at higher levels in the waste body. The presence of perched bodies of water can cause difficulties in understanding leachate storage from simple observation of leachate levels.

The rate of infiltration of leachate through waste is the main factor affecting the time needed to achieve waste stabilisation. Consequently, an understanding of the landfill water balance will give an indication of the design life of the site and its monitoring system.

### Leakage rate and location

Whilst well engineered landfill sites are unlikely in the short term to leak at rates which will cause any significant impact on water receptors, even the best engineered landfill sites will leak to some extent. This principle underlies the design of all modern landfill sites. It is important that careful assessment is made of any landfill to ensure that the site-specific design complies with both the Landfill and Groundwater Directive.

The rate and location of leakage is determined by:

* The type of material forming the base, sides and capping to the site.
* The head of leachate on the base and sides of the site.
* The groundwater level or piezometric head outside the site and
* The presence of preferential flowpaths (e.g. overspills to surface, boreholes penetrating the landfill base or other damage to engineered containment structures).

The presence of preferential flowpaths can dominate leachate egress from any site, and monitoring should take account of potential design weaknesses as well as designed leakage mechanisms, such as seepage through the site base.

### Designed leakage – ‘acceptable release rates’

The concept of an ‘acceptable release rate’ for landfill lining systems is a recognition that all engineered structures do leak to some extent and have a defined lifetime and design limitations. Whilst it is possible that the best of engineered landfill sites will contain and control leachate with minimal leakage, there is always a probability that some failure in engineering will occur.

Groundwater quality may change as a result of leakage of leachate through the landfill liner system. Design performance standards, including risk-based limits of acceptable leakage (which take into account the physical and attenuating properties of the lining system), should have been agreed between the operator and SEPA at the time of site design. These will have based on the need to comply with the Groundwater and Landfill Directive. Groundwater control and trigger levels should be specified and used to determine if the site is performing as designed and/or if it is causing a significant adverse environmental impact. These control and trigger levels should encompass a range of indicator chemical determinands and should be reviewed in the light of ongoing monitoring data.

Detecting water quality changes and identifying clear breaches of established limits can be a complex process, particularly in the presence of natural cyclic variations in quality and diverse land use practices surrounding many landfill sites. Further guidance is provided in Chapter 7.

Designed leakage may be:

* Diffuse, as in the case of a well-engineered mineral or composite liner and
* Discrete, as in the case of a flexible membrane liner with the potential for pinhole or tear damage.

Where discrete leakage is possible, monitoring programmes will need to be designed to detect leakage from small point sources - e.g. possibilities include a leachate detection layer, resistivity array in the unsaturated zone and strategically spaced groundwater monitoring boreholes.

In comparison, diffuse leakage offers two advantages.

## Waste types, landfill design and leachate

### Groundwater

The behaviour of groundwater is a complex subject forming a science in its own right. Once leachate emerges at the base of a landfill, it will begin to disperse. The direction and rate of this dispersal will be determined by:

* The properties of the soil or rock (geology).
* The prevailing groundwater flow conditions (hydrogeology) and
* The presence of man-made or natural voids (e.g. mineshafts).

A conceptual model of the site in relation to the geology and hydrogeology surrounding it is essential to be able to determine contaminant flow paths and flow rates, which will in turn be used to decide on monitoring locations and frequencies.

In terms of groundwater flow, the subsurface may be divided in general into two generalised physical zones:

* The unsaturated zone (above water table) and
* The saturated zone (below water table).

Water movement through the unsaturated zone is predominantly downward (gravity driven) until it reaches the water table. Flow through the saturated zone will follow the prevailing groundwater gradient. In granular formations without fissures or conduits, unsaturated zone flow is commonly much slower than saturated zone flow, though flow rates can still vary over several orders of magnitude. When fissures or conduits are present, flow rates can approach those found in surface waters. (See Section 6.4.6).

### Surface water

In comparison with most groundwater flow, surface water flow may be:

* Rapid, with the result that contaminants can be transported to a receptor in minutes to hours, rather than days to years.
* Of high volume, offering large dilution of contaminants.
* Seasonally variable and liable to rapid fluctuations over short time periods resulting in large variations in dilution potential and
* Capable of carrying contaminants within sediment load as well as in solution.

The consequences of these factors are that risk assessment should be cautious and take account of the lowest flows in surface water courses, and frequency of high intensity rainfall events (necessitating careful timing of flow monitoring). Furthermore, quality monitoring should be designed with an understanding of the short travel times involved. This latter issue can be resolved in two ways:

* By accepting that quality monitoring is a ‘spot check’ rather than an effective early warning system and
* By monitoring at more frequent intervals related to travel time, or continuously in situations where downstream receptors are sensitive to short term contaminant loadings.

Biological monitoring of surface waters can detect pollution incidents that have occurred in the preceding weeks or months. This type of monitoring also provides an opportunity to detect pollution by its effects, rather than relying on a set of chemical analyses that may or may not include the specific pollutant.

### Attenuation of leachate-derived contaminants

Attenuation is the decrease in contaminant concentration or flux through biological, chemical and physical processes, individually or in combination (e.g. dilution, adsorption, precipitation, ion-exchange, biodegradation, oxidation, reduction).

**Attenuation in groundwater**

As water flows through soil and rock in both the unsaturated and saturated zone, there is a continuous interaction between substances dissolved in the water and substances in the soil or rock. These processes may lead to attenuation of contaminants in groundwater. There is an increasing body of research investigating the practicalities of utilising attenuation mechanisms for controlling the impacts of contaminant migration and specific guidance is not given in this document.

**Attenuation in surface water**

The principal means of attenuation in surface water is dilution caused by advection and dispersion. Other (slower) processes include deposition and adsorption onto sediments, volatilisation and degradation of contaminants.

**Reliance on attenuation mechanisms**

Where attenuation is relied upon in any site, monitoring programmes need to be specifically tailored to identify in detail the flow mechanisms, attenuation processes at work and the capacity of these mechanisms to reduce the concentration of contaminants. In these instances, a robust risk assessment is essential.

## Effects of leachate on receptors

Receptors may be of value in one or more of the following categories:

* Groundwaters and Surface waters.
* Abstractions - public and private water abstractions for potable, industrial, agricultural or other legitimate use.
* Biodiversity (ecological value)- surface water bodies, including wetlands supporting a variety of living organisms or
* Amenity - a surface water body used for leisure pursuits (e.g. fishing, sailing).

Leachate contamination may affect receptors in a number of ways depending on the contaminant loading of leachate and the nature of the receptor. A summary of some of the potential effects is given in Table 2.1.

A reasoned design of monitoring programmes for a landfill requires a risk assessment to be undertaken to identify and prioritise risks to each potential water receptor in the vicinity of the site (Chapter 4).

**Table 2.1a: Some potentially deleterious properties of leachate on water receptors – Primary impacts (EXAMPLE)**

| **Leachate component** | **Short term impact** | **Long term impact** |
| --- | --- | --- |
| High suspended solids | Reduction of light-inhibiting macrophyte growth, sedimentation causing smothering of aquatic life, organic particles increasing deoxygenation through microbial breakdown. | Habitat alteration, adsorbed pollutants increase toxicity. |
| High dissolved solids | Increased salinity altering ecology and reducing value of surface waters for abstraction. | Groundwater contamination. |
| Dissolved toxic compounds | Direct toxicity to humans (e.g. toxic metals, trace organic compounds) or to aquatic life (e.g. from ammonia toxicity to fish). | Biomagnification, Bioaccumulation |
| Immiscible organic chemicals mutagenic (e.g. oils and solvents) | Direct toxicity, reduction in reoxygenation rates through water surface, oil coating of plants and animals. | Carcinogenic and effects on aquatic life.  Deoxygenation. |
| High oxygen demand | Deoxygenation of surface water. Few plants, invertebrates or fish can survive. | Deoxygenation, ecosystem changes total deoxygenation. |

**Table 2.1b: Some potentially deleterious properties of leachate on water receptors – Secondary (minor) impacts (EXAMPLE)**

| **Leachate component** | **Short term impact** | **Long term impact** |
| --- | --- | --- |
| Organic and biological contamination | Reduced oxygen levels. Contamination of surface waters used for: human potable supplies, irrigation of food crops and recreational waters. | Deoxygenation, ecosystem changes. Possible contamination of potable groundwater resources. |
| Nutrients (e.g. nitrate) | Plant / algal blooms. | Eutrophication. |
| Gassing | Direct toxicity to aquatic life. |  |

# Monitoring Principles

## Introduction

This chapter sets out a number of key principles underpinning the more detailed guidance on monitoring of landfill leachate, groundwater and surface water given in Part 2 of this document.

## Purpose and context of monitoring

### Purpose of monitoring

Monitoring should be undertaken and designed in order to comply with the requirements of the Groundwater Regulations and the Landfill (Scotland) Regulations 2003.

Monitoring is also a central part of the landfill risk assessment and management process and is undertaken to gain information before the start of operations (to determine baseline conditions) and during the lifetime of the site.

Monitoring includes measurements undertaken for compliance purposes and those undertaken to assess landfill performance. The terms compliance and assessment monitoring can be defined as follows:

* Compliance monitoring should be undertaken to indicate that a regulatory standard is met; For example, that a trigger level has not been breached and
* Assessment monitoring should be undertaken to evaluate if a significant departure from expected conditions by reference to an adverse trend in data or the breach of a specified limit. Control levels should be set for groundwater to assess this.

Specific purposes for monitoring leachate, groundwater and surface water are to:

* Define baseline (background) water quality and physical conditions in surrounding groundwater and surface water.
* Allow assessment of compliance with site licence conditions.
* Provide confirmation that landfill engineering measures are controlling leachate as designed.
* Provide information about the processes occurring within the landfill site.
* Provide information on the state and rate of stabilisation of the waste body for comparison to the design lifetime of containment and monitoring systems.
* Provide an early warning of any departure from design conditions.
* Provide an early warning of adverse environmental impacts.
* Provide an early warning of breach of regulatory standards.
* Provide information to enable decisions on the management of the site to be taken and
* To provide information to support an application for a certificate of completion.

Where pollution is identified as arising from landfill leachate, or for older “dilute and disperse” sites, the monitoring programme is also a means to:

* Determine the nature, extent and rate of migration of contamination from the site.
* Provide data to support predictions of the future impact of leachate on receptors.
* Provide data to justify reliance on natural attenuation processes.
* Justify and monitor remediation measures and
* Provide data to support or justify regulatory action.

### The monitoring process in the context of site management

Monitoring should be considered as part of the overall quality management system of every landfill site development with the purpose of demonstrating whether design standards have been met and whether the long-term integrity of the site is assured. Monitoring has a central and continuous role to play throughout the planning and permitting phases of every landfill site, only ending on issue of a certificate of completion.

Within this framework, the primary monitoring processes involved are to:

* Establish objectives and standards in relation to risk (see Chapters 4 and 5).
* Design monitoring programmes to meet objectives (Chapters 6 and 7).
* Install and maintain monitoring infrastructure (Chapter 8).
* Gather monitoring data (Chapter 9).
* Compare monitoring data with design objectives to indicate success or failure (Chapter 10) and
* Respond to any leachate impacts (either by further monitoring or remediation) (Chapters 7&10).

The approach to monitoring adopted in this guidance requires that monitoring should be:

* Quality assured.
* Based on an understanding of the risks posed by the site and
* Statistically justifiable.

These issues are dealt with in the following three sections.

## Quality assurance

Data gathered during monitoring programmes need to be reliable and fit for their intended purpose. Quality assurance (QA) and quality control (QC) should be incorporated into all elements of the development of monitoring infrastructure and monitoring programmes. Documentation specifying QA procedures should be included within the site control and monitoring programme.

Quality assurance plans should specifically address the certification of monitoring infrastructure (Chapter 8).

This should be seen as an extension of normal construction quality assurance (CQA) procedures applicable to other landfill engineering practices.

* Consideration of appropriate methods of sampling, laboratory analysis, data handling, interpretation and reporting (Chapter 9) and
* Quality Control procedures used to assess the adequacy and appropriateness of sampling and measurement strategies (Chapter 9).

## Monitoring in relation to risk

### Risk assessment

Landfill monitoring should be targeted to assess the risks that the site poses to the environment. The risk assessment process should result in the identification of all water receptors and help identify the potential migration pathways between the landfill source and each receptor. A risk of pollution can only occur if these three elements (source-pathway-receptor) are linked.

The risk assessment process needs to establish whether the site complies with the Groundwater Regulations and Landfill Regulations.

### risk-based monitoring

This guidance formalises the risk-based approach to monitoring by recommending a risk-based monitoring approach to monitoring programmes at a landfill. The risk-based monitoring assessment should follow on from and use technical information from the hydrogeological risk assessment and for groundwater should be focused on the incorporation of control and trigger levels. It will present a conceptualised model of the source-pathway-receptor relationships for the landfill culminating in a “risk-inventory” to rationalise and prioritise which pathways and receptors need to be monitored. The risk inventory should form the basic design tool for specifying the details of monitoring locations and schedules. The preparation of the risk-based monitoring assessment is described in Chapter 4.

## Statistical aspects of monitoring

### Introduction

The design of monitoring programmes and the interpretation of data should follow sound statistical principles. For example, a statistical understanding of the variation of a measurement prior to commencement of landfill construction and operation may help to:

* Avoid wrongly attributing changes in the measurement to the impact of landfill leachate and
* Provide a justification for increasing or decreasing the sampling frequency, or for changing the analytical method and quality control procedures.

Statistical principles applied to good laboratory practice are described in the document published by the Standing Committee of Analysts, 1996[[1]](#footnote-1) and in other standard texts[[2]](#footnote-2).

The two areas where statistical methods are most applicable to monitoring are:

* Monitoring programme design, i.e. the collection of a valid baseline data set, the choice of measurement frequencies and the specification of the reliability of measurement methods and
* Assessment of monitoring data, i.e. the use of appropriate statistical tests to determine whether an impact is significant.

Guidance on the principles and terminology used in this document is provided in the following sub-sections.

### Baseline data

To be able to use monitoring data to detect impacts from leachate, the normal pattern of variation in a monitoring record needs to have been established at an early stage in the monitoring process.

Baseline (or background) monitoring data are defined in this document as measurements that characterise physical, chemical or other distinctive properties of groundwater and surface water unaffected by leachate contamination. Monitoring data, including those collected during and after operation of the landfill, remain part of the baseline record until a significant deviation from the established pattern of baseline variation is identified. It is important to note that this definition of baseline refers to data and not to any particular monitoring points or monitoring programmes.

Data can be compared with baseline monitoring records in two ways:

* Comparison with the historic baseline. This may be undertaken by comparing data from individual or groups of monitoring points with historical trends in the same monitoring point(s) and
* Comparison with up-gradient or remote monitoring points. This may be undertaken by comparing individual or groups of monitoring points down-gradient of the landfill with up-gradient or remote monitoring points in the same groundwater body.

### Specifying reliability and frequency of measurements

To specify the reliability and frequency of a measurement, it is necessary to have an understanding of the certainty with which the measurement results must be known. This in turn is determined by the baseline variability of that measurement, and the amount of deviation from the norm that would give cause for concern (significant deviation). This subsection defines these concepts as they are used in this guidance.

**Uncertainty**

Ideally monitoring measurements should represent the actual conditions being sampled, and should not be subject to uncertainty. In practice however, all physical, chemical and biological measurements have errors associated with them. The presence of these errors leads to a degree of uncertainty in the quoted result. Uncertainty has been defined in numerical terms as:

‘the interval around the result of a measurement that contains the true value with high probability’ (Thompson, 1995).

Uncertainty in a final measurement result arises from the following sources:

* Poorly understood variations which occur naturally (e.g. seasonal variations) or as a result of contamination[[3]](#footnote-3).
* Random fluctuations in the performance of the sampling and measurement systems (random errors) and
* Bias introduced by the sampling and measurement systems (systematic errors). Unless it can be predicted and corrected, bias is also a source of uncertainty.

Sampling and measurement errors affect the accuracy and precision of measurement results (see Section 9.13.2).

**Baseline variation**

A baseline monitoring record will display variations in data that incorporate all of the above sources of uncertainty to a greater or lesser degree. The total variability in a measurement value in the absence of landfill development can be identified from a good baseline record. For practical monitoring purposes, the initial baseline variation should be determined following the initial period of characterisation monitoring.

**Significant deviation**

The significant deviation may be estimated by a fixed limit value used either for compliance or assessment purposes. In these situations, the reliability of the data in relation to the fixed limit value becomes critical. The closer data are to the limit value, the more reliable they need to be (i.e. uncertainty needs to be minimised).

In other situations, the choice of significant deviation may be an operational decision (e.g. to provide adequate warning of a potential problem) or be related statistically to baseline variability.

The use of limit values and assessment criteria to define significant deviation is discussed further in 3.6.4 below, and in Chapter 7.

**Tolerable uncertainty**

The purpose of a measurement should be to provide a result so that it is possible to distinguish a significant deviation from the ‘normal’ variability of that measurement. The ‘tolerable uncertainty’ for a measurement is defined here as the degree of uncertainty that is acceptable without compromising the purpose of the measurement.

Tolerable uncertainty is specified by the operator to enable effort to be focussed on measurements where greater reliability is required, and to avoid wasted effort where reliability is less of an issue. A tolerable uncertainty should be specified, as a minimum, for all ‘indicator’ monitoring measurements, and preferably for all measurements. It may be stated as a fixed variation (e.g. ±10mg/l) or as a percentage variation (e.g. ±25%) in the value of a measurement, as long as it achieves the purpose of expressing how certain a measurement needs to be.

In general, where measurements are close to compliance limits, the tolerable uncertainty needs to be as low as possible (i.e. greater quality assurance is needed). For measurements which are well below compliance limits greater tolerable uncertainty may be acceptable, depending on how significant deviation has been defined for that measurement.

Tolerable uncertainty values can only be fully defined for a measurement after:

* Sufficient baseline data have been collected - the results of initial characterisation monitoring and any other subsequent baseline data are used to define the value and variability of the measurement in the absence of the landfill; and
* The likely value of any assessment or compliance limit is known this defines the value of the measurement that would give cause for concern.

Since initial characterisation monitoring has to be carried out before tolerable uncertainty is known, any initial monitoring needs to be undertaken with a high degree of quality assurance (Section 9.13) assuming low tolerable uncertainty for all measurements.

Once tolerable uncertainty values are established, these will help guide the most appropriate choice of:

* Quality control effort.
* Methodology for obtaining samples.
* Methodology for performing measurements.
* Sample frequency and
* The number of samples needed.

The concept of tolerable uncertainty therefore allows sampling programmes to be designed in order to achieve results that are appropriate for their intended purpose. For this reason, the term ‘appropriate sample’ is used in this guidance in preference to ‘representative sample’ (the latter term implies that uncertainty will be kept to a minimum at all costs). Use of appropriate sampling should mean that effective monitoring is carried out for minimum cost and effort. Tolerable uncertainty is not in itself a regulatory tool, although failure to apply the concept may lead to ineffective monitoring or unnecessary breaches of assessment limits, both of which would be the subject of regulatory attention.

Further guidance on specifying tolerable uncertainty is given in Section 6.3.5. Further discussion of errors and sampling quality control is provided in Chapter 9.

### Assessing monitoring results

For monitoring to serve its purpose, data must be assessed in relation to a limit value or measure of significant deviation. An ‘assessment criterion’ is a statistically robust means of determining whether a limit (either an assessment or compliance limit) has been breached or an adverse trend has developed e.g. has a control or trigger level been breached.

Assessment criteria should be set:

* With due regard for the normal pattern of variation in the absence of the landfill, so that natural changes are not mistaken for landfill impacts and
* To detect genuine impacts as early as possible.

Circumstances may arise at some sites where there is ambiguity in differentiating between an impact arising from a landfill, and the normal pattern of variation, particularly where other external sources of contamination are present. In these situations, consultation will be required between the site operator and SEPA to establish assessment criteria in the light of site investigation and monitoring results.

Assessment criteria should be proposed by the operator and agreed by SEPA. Where an unacceptable impact is confirmed to be due to leachate, predetermined contingency actions would need to be implemented.

Guidance on assessment criteria is given in Chapter 7.

### Data management

The collection of large amounts of monitoring data necessitates the development of data management systems. Data need to be collated in a format which allows flexibility for data analysis and presentation whilst safeguarding the integrity of the data. Data management should involve means of validating and maintaining the quality of data. For example, any data stored and manipulated on computers need to be carefully validated and cross-referenced against other archived paper records and original source material (Section 10.7).

Presentation of data in tabular and graphical formats, which are clear and intuitively understandable to personnel unfamiliar with a particular landfill site, is an important part of data management. A number of computerised geographic information systems (GIS), database and spreadsheet systems now make data management easier, and landfill operators are encouraged to utilise such systems for reporting purposes. Further guidance on the storage of data and information requirements for reporting is provided in Chapter 10. Additional guidance on the use of graphical statistical methods for representing data trends is provided in Chapter 7.

## Introduction

This guidance groups landfill monitoring programmes into five categories:

* Initial characterisation monitoring of groundwater and surface water.
* Routine monitoring of groundwater and surface water.
* Leachate characterisation monitoring.
* Assessment monitoring and
* Completion monitoring.

In addition to the above, SEPA will periodically undertake audit monitoring.

Monitoring of processes other than the landfill itself (e.g. fuel storage, discharge consents, leachate treatment) should also be managed as part of the integral monitoring of the site. Guidance for these does not form part of this document.

Explanatory notes for each of the five categories of monitoring programme are provided in the following sub-sections.

### Assessing monitoring results

Initial characterisation monitoring is a period of monitoring to define the normal range of variation in surface water and groundwater. The frequency and range of monitoring data collected need to be sufficient to be able to characterise seasonal and other non-landfill influences. A broad range of measurements is required because in most cases, detailed characterisation of the water will not have been historically undertaken, and the detailed nature of future impacts could not be fully predicted. For groundwater, the Landfill Directive requires that, as a minimum, sampling must be carried out at three locations before filling operations begin.

For new sites, initial characterisation monitoring needs to be completed prior to commencement of infill in order to draft assessment and compliance conditions into the site control and monitoring plan. At older operational or closed sites, where historic monitoring data are absent or inadequate, initial characterisation monitoring may need to be initiated at a later stage, using monitoring locations which are representative of conditions unaffected by the landfill.

### Routine monitoring of groundwater and surface water

Routine monitoring of groundwater and surface water is undertaken to maintain continuity with the initial characterisation monitoring programme and to concentrate effort on comparing the performance of landfill operations with assessment and compliance limits. Routine monitoring can be divided into two parts as follows:

* **Indicator measurements**: to provide more frequent monitoring of measurements specified for compliance purposes and including a number of additional parameters capable of indicating impacts by leachate. Parameters to be measured most frequently would be selected from the results of initial characterisation monitoring programmes and incorporate anticipated leachate indicators (e.g. ammoniacal-nitrogen, chloride and TOC are likely to be selected for biodegradable landfill sites). As the results of initial leachate characterisation monitoring become available, indicators may need to be revised to reflect measured leachate characteristics and
* **Ongoing characterisation measurements**: a periodic repeat of the same measurements that were undertaken during the initial characterisation monitoring programme but at a lesser frequency. This provides a periodic screening of all monitoring measurements. Other monitoring requirements may also be incorporated (e.g. requisite surveillance of groundwater as required by the Groundwater Regulations).

### Leachate characterisation monitoring

Leachate characterisation monitoring is undertaken to provide a ‘benchmark’ of the source pollutant. Due to the complexity of processes involved in the production and evolution of leachate, significant variations are likely to occur in the composition and physical characteristics of leachate with time and between different parts of the landfill. Any monitoring regime needs to be sufficiently flexible to respond to site-specific changes that may occur in leachate levels and composition. It is usually during the process of infilling and restoration of the site, and the early stages of leachate production that the greatest uncertainties arise in both the hydraulic performance of a landfill and in leachate quality. More intensive monitoring at these early stages is needed to maintain confidence in the capability of the landfill to maintain leachate levels below specified maxima and to demonstrate that leachate quality falls within the design parameters used for risk assessment or compliance purposes.

In this document, leachate characterisation monitoring is divided into two parts as follows:

* Initial leachate characterisation monitoring and
* Routine leachate monitoring.

**Initial leachate characterisation monitoring**

This is an initial period of detailed monitoring undertaken until a recognisable pattern of change in leachate level and composition has been established. Typically, this would continue for a minimum period of 2 years following restoration of a landfill cell. Initial leachate characterisation monitoring should begin as soon as possible after the first deposit of wastes even if early results simply confirm the absence of free leachate.

Other characterisation monitoring programmes (e.g. screening of leachate quality for List I and List II substances as part of a hydrogeological risk assessment) could also be initiated at this stage.

**Routine leachate monitoring**

Routine monitoring of leachate is undertaken primarily to compare the performance of landfill operations with conditions specified by the site licence or working plan and consists of:

* **Leachate indicator measurements**: to provide more frequent monitoring of measurements specified for compliance purposes, and additional parameters which are likely to vary significantly between characterisation surveys. For example, parameters to be measured most frequently could be those needed for monitoring landfill design criteria (e.g. leachate levels) and
* **Ongoing leachate characterisation measurements**: a periodic repeat of the same measurements that were undertaken during the initial leachate characterisation monitoring programme but at a lesser frequency. (Other monitoring requirements such as periodic screening of leachate for List I and List II substances, for the purpose of validating a hydrogeological risk assessment, could also be considered to form part of ongoing characterisation monitoring).

### Assessment monitoring

Assessment monitoring may include a combination of a greater intensity of monitoring (e.g.

more frequent monitoring combined with an increased range of measurements) or site investigation.

The need for assessment monitoring could be triggered by a number of situations. For example, where significant departures from baseline or design conditions are identified (e.g. breach of a control level), or where a greater degree of monitoring information is needed to define natural attenuation and migration processes.

### Completion monitoring

Completion monitoring is part of a process conducted towards the end of a site’s licensed lifetime in order to demonstrate that the landfill is no longer capable of harming human health or the environment.

Completion monitoring requires that a trend of improving leachate quality has been established by ongoing monitoring programmes. Consequently, all monitoring data collected up to this point will form an essential part of the detail needed to demonstrate completion conditions. A completion report is needed to support the application to surrender a permit and to demonstrate that waste stabilisation has been achieved. This may necessitate reinvestigation, a period of more intensive monitoring and a re-appraisal of risk.

### Relationship of monitoring programme categories to landfill stages

Monitoring programmes are often categorised based on four defined stages in the lifecycle of a landfill site:

* Stage I: Investigation and preparatory phases, both for planning and permitting purposes (pre-landfilling).
* Stage II: Operational phases (landfilling and final restoration).
* Stage III: Post closure and aftercare period (site closure up to surrender of licence or permit) and
* Stage IV: Site completion (surrender of licence or permit).

The concepts of initial characterisation, routine and assessment monitoring do not always fit comfortably within these stages. For example, initial characterisation monitoring of groundwater and surface water should ideally be completed during Stage I. However, at existing operational or closed sites, where historic monitoring data are absent or where poor monitoring has been undertaken to date, it may extend into Stage II or even Stage III. Routine monitoring should be the normal standard of monitoring from Stage II up to site completion (Stage IV). Assessment monitoring could occur at any stage to demonstrate, For example, natural attenuation or to investigate anomalous trends in monitoring data.

## The Site Control and Monitoring Plan

The technical specification for all landfill monitoring programmes should be incorporated into a single, updateable document - the site control and monitoring plan. This should include the proposed monitoring and sampling programmes, assessment criteria and compliance levels, the contingency action plan and the reporting procedure. Guidance on the contents of the site control and monitoring plan is presented in Part 2. The site control and monitoring plan should be reviewed by the site operator and updated regularly. Any changes should be agreed with the SEPA.

# Risk-Based Monitoring

## Introduction

The development of a landfill monitoring programme which is risk-related needs to be based on a thorough understanding of the site setting, the sensitivity of the surrounding groundwater and surface water to leachate pollution and the potential migration pathways between the site and each receptor. An understanding of the site conceptual model and an understanding of the source-pathway-receptor linkage is therefore an essential prelude to the proper design of a monitoring programme. **In most circumstances there will be no need for duplication of effort or reporting as the risk-based monitoring programme will be determined as part of the hydrogeological risk assessment process**.

The hydrogeological risk assessment should:

* Produce a conceptual model of the site and surrounding area.
* Determine the essential and technical precautions that should be taken.
* Provide a technical rationalisation for the design of a monitoring programme and
* Determine appropriate control and trigger levels for the site.

Accordingly, the hydrogeological risk assessment should result in the identification of risk-based monitoring objectives, particularly in respect of groundwater control and trigger levels that will have been derived during the assessment.

In the absence of a risk assessment, a separate risk-based monitoring review should be undertaken. The information that this review use, and its outputs should be similar to those of a hydrogeological risk assessment although the outputs should be focused exclusively on the monitoring requirements rather than the technical precautions.

A review of water receptors at risk, and how these can be effectively monitored presents technical and commercial benefits for operators and technical benefits for SEPA. For example,:

* At any type of landfill where there are few receptors at risk, a risk-based approach to monitoring may provide the means to justify relaxation of monitoring programmes and
* At any type of landfill where risks to receptors from landfill leachate are significant, a risk-based approach to monitoring will enable efforts to be appropriately justified and targeted.

Guidance in this chapter is presented in two parts:

* Section 4.2: describes the process of undertaking a risk-assessment for use in designing a monitoring network and
* Section 4.3: describes the documented outputs of the risk-assessment, which should be incorporated into the site control and monitoring programme.

## The Risk-Assessment Process

### Introduction

The objective of the risk-based approach to monitoring is to bring together (and, if necessary, supplement) the data on risks to receptors and to provide a documentary record of the information used in designing the monitoring programme (see Section 3.4).

Some of the data and risk assessments, which are required in order to design a risk-based monitoring programme, may already have been included within other documents (e.g. hydrogeological assessment or site reports) in which case reference to these will be acceptable. For new sites, a risk-based monitoring plan should be included as part of the planning and permitting process.

### Risk-based Monitoring Development Tasks

For a new landfill, the main effort in developing a risk-based monitoring programme would be at the start of the site planning or permitting process. For currently operating landfills the initial monitoring programme would itself need to be periodically reassessed. Specific tasks involved in designing a risk-based monitoring programme are:

* Identification of all receptors at potential risk.
* An initial review of the risks posed by the site to the individual receptors throughout its lifetime and afterwards. This should include a consideration of the predicted impacts which the site will have on these receptors.
* Determination of the maximum impact which the site could have on receptors before an adverse environmental impact would be considered to have occurred so that assessment limits can be set (e.g. trigger levels).
* Prioritisation of risks to individual water receptors for monitoring purposes and
* Periodic reassessment of risks to receptors during the lifetime of the site. This should be undertaken in the light of the results of monitoring (particularly where there is any evidence of leachate impact), in response to changes in the development of a landfill, or where changes in surrounding land usage influence groundwater or surface water flow or quality. The maximum interval between reassessments should be no greater than that required to comply with the Groundwater Regulations (maximum four years). Breach of control or trigger levels could prompt earlier reviews.

### Information Requirements for Risk-Based Monitoring Development

The risk-based monitoring review involves gathering technical information on the site design, construction, history and waste input alongside information on surrounding surface water and groundwater and other individual receptors at risk. Groundwater and surface water should be evaluated as both pathways and receptors. In designing the risk-based monitoring plan the site should be placed within defined surface water and groundwater catchment areas so that all external sources of contamination, which may influence monitoring results, are clearly identified.

The process of reviewing information may be a desk exercise for sites with existing site investigation information and risk assessment. Other sites may require specific site investigation.

An example list of information to be collated and reviewed is presented in Table 4.1. For small sites with receptors at low risk, most of the information may be summarised in simple tabular format combined with a catchment plan incorporating brief comment on the risks. For sites with receptors at greater risk, more detail will be needed.

### Uncertainties in Risk Assessment

It is possible that uncertainties will be revealed by the risk-based monitoring plan, which can only be resolved by ongoing monitoring or investigation. For example,:

* Ambiguities arising as a result of contamination by neighbouring land usage; and
* Unusual natural water quality variations.

Even where risks to receptors are difficult to define, a site control and monitoring plan may still be formulated. The monitoring plan should address uncertainties on a case-by-case basis as agreed in consultation between the operator and SEPA. Specific objectives should be established for monitoring and further investigation. Where a site control and monitoring plan is being prepared prior to the issue of a permit, a statement should also be included which clarifies at what stage of monitoring or investigation a site permit could reasonably be issued.

## Documentation to Accompany the Design of a Risk-Based Monitoring Programme

### Review outputs

Information which may be useful to incorporate into the site control and monitoring plan are as follows:

* Landfill catchment drawings (conceptual model) to illustrate a conceptual understanding of the groundwater and surface water catchment areas identifying hydraulic relationships between the landfill and receptors at potential risk.
* Landfill characterisation details summary of landfill geometry, waste input and design details which help to define the hazard posed by the site to groundwater and surface water.
* Catchment details summary of rainfall, catchment areas, land usage, water quality standards and other regulatory standards applicable to groundwater and surface water in the defined catchment areas and
* Site Conceptual Model and Risk inventory summary of receptors, pathways and risk prioritisation as a tool for directing monitoring effort.

Elements of each of these issues are highlighted in the following sections.

#### Table 4.1: Summary of EXAMPLE information required to design a risk-based monitoring programme.

**The landfill site**

Site geometry (area, depth, volume, cell structure)

¾ waste type (either proposed, or recorded by waste input monitoring)

¾ operational methods (infill rate, compaction methods, cover methods)

¾ in-situ waste properties (density, permeability)

¾ leachate composition

¾ engineering design

¾ liner properties and basal leakage calculations

¾ other leakage mechanisms

¾ discharge points and consents

¾ surface run-off

¾ other contaminant sources

**Surrounding land use and historical land development**

Identification of man-made conduits (e.g. mine shafts / adits / workings, drainage features / field drains / culverts, boreholes / wells, service trenches / pipelines, tunnels)

¾ identification of external sources of contamination (e.g. contaminated land, road drainage, septic tanks, soakaways, agriculture, industrial and domestic discharges, sewage treatment works)

¾ characterisation of impact on water quality and quantity from external sources at site boundary (baseline)

¾ receptors at risk (developments, amenities)

**Rainfall and catchment statistics**

Rainfall statistics (based on Met Office Agency or site records)

Catchment area (up-gradient and down-gradient areas)

**Hydrology (surface water features)**

Identification of surface water features within site catchment area and on-site

¾ a review of relationship between groundwater flow and surface water features

¾ quantification of surface water flows

¾ surface water quality standards

¾ characterisation of surface water quality (baseline)

¾ ecological features

¾ receptors at risk, pollution pathways, transport and attenuation mechanisms

¾ discharge and disposal routes for leachate

**Geology and Hydrogeology (groundwater systems)**

Description of geology / identification of natural voids

Identification of groundwater systems (plans and cross-sections)

Description of unsaturated zone

¾ hydraulic characteristics (direction, quantity and rate of flow)

¾ classification of groundwater systems and water quality standards, including groundwater vulnerability classification

¾ receptors at risk (e.g. groundwater, springs, abstractions), pollution pathways, transport and attenuation mechanisms

### Landfill Catchment Drawings

To aid a conceptual understanding of the site setting in relation to surrounding groundwater and surface water, at least one catchment drawing encompassing the landfill site and any receptors at risk should be prepared.

Catchment drawings can usefully be supplemented by aerial photographs to illustrate land usage and geographical features including surface water drainage patterns.

For smaller sites in relatively simple hydrological settings, it may be possible to produce a single catchment drawing, which encompasses all the relevant water interests in the area. For larger sites in more complex environments, a series of drawings may be necessary to differentiate, For example, between groundwater flow in multiple systems, or to illustrate the catchment areas to individual groundwater and surface water receptors.

Groundwater catchments may be irregularly shaped where flow is influenced by fissure flow, man-made conduits, pumping from boreholes or dewatering operations. The production of groundwater catchment maps in most cases will be a matter of judgement based on an understanding of the local hydrology and hydrogeology, but it should be recognised that there are many inherent difficulties and uncertainties in producing these. Where uncertainties exist which are relevant to the design of a monitoring programme, catchment boundaries should be reviewed and agreed with SEPA.

In general, the following will apply:

* Groundwater catchment drawings should be provided for each groundwater system identified in which there are receptors at potential risk. These should illustrate the recharge area up-gradient of the landfill site and the discharge points down-gradient. The area down-gradient of the site, which could potentially be affected by leachate contamination, should be drawn making allowance for possible lateral dispersion of contamination diverging from flow lines. Groundwater level contours should be shown.
* Surface water catchment drawings should be provided for each discharge point from the site at the point of entry into an off-site water course.
* Additional surface water catchment plans may be needed corresponding with the points of discharge to surface water courses from groundwater seepage.
* Where other external land users impact on the same water systems, catchments for these may also need to be shown.
* Abstractions and other receptors should be shown on the catchment drawings. Deflection of groundwater contours in the vicinity of groundwater abstractions should be shown to illustrate the recharge capture zone for each source and
* Catchment drawings should clearly show geographical features and include a scale and north-point.

The purpose of these drawings is:

* To place the landfill in the context of surrounding land use to identify the potential influence of the landfill and neighbouring activities on groundwater and surface water within the catchment.
* To identify the hydraulic relationship between water receptors in the area of the landfill site For example, wetlands, boreholes, groundwater seepage to stream courses and
* To define the area available for groundwater recharge up-gradient of the site to provide information to support groundwater flow calculations.

### Landfill Characterisation Details

A summary of the main elements of the landfill site design and waste input should be provided. Where large quantities of data are involved, these should be summarised with descriptive statistics[[4]](#footnote-4). Information provided should be relevant to monitoring. The following is a checklist of information which, if relevant for the site, should either appear in the risk-based monitoring review or be readily available and clearly referenced:

* A site plan identifying:
  + - * The area of the site to be landfilled.
      * The cell structure in existence or planned.
      * The location of any surface water features (including culverts).
      * Site drainage arrangements, including the location of any existing or proposed discharges from the site and
      * The location of any other site facilities with the potential to introduce contamination to groundwater or surface water.
* A table summarising the quantity of proposed or actual waste types deposited at the site.
* A statement of operational methods and waste properties, i.e. rate of filling, compaction and cover methods, measured or calculated waste density and permeability.
* A table or series of tables summarising the conditions applicable to any discharge/ trade effluent consents issued by the SEPA or a water utility, together with any available data on the actual quality of these discharges.
* For sites in which leachate control is an integral part of the landfill design, a table or series of tables should be produced for each separate landfill cell in the site summarising the following information (all levels should be expressed as m.AOD[[5]](#footnote-5)):
  + - * The minimum and maximum base levels of each cell.
      * The minimum and maximum level of any intermediate retaining walls surrounding each cell.
      * The actual or proposed minimum restored surface level of each landfill cell before and after settlement and
      * Maximum recommended or actual leachate level to be used for permit control (this should be based on the hydrogeological risk assessment).
* A table summarising the assumed leachate quality used in a risk assessment of the site including for each determinand:
  + - * Maximum and minimum assumed values.
      * Most likely assumed value, and assumed variation over time and
      * Any other relevant statistics.
* A tabular summary of attenuating properties of the lining system at the base of each landfill cell (where relevant to the risk assessment) including:
  + - * Type of liner.
      * Maximum and minimum thickness of lining system.
      * Hydraulic conductivity descriptive statistics (estimated and / or measured).
      * Cation exchange capacity descriptive statistics (estimated and / or measured).
      * Descriptive statistics for any other attenuating properties used for design purposes.
      * Maximum acceptable and predicted leakage rate and
      * Assumed overall attenuation factor for specific determinands assumed in site design.
* For sites with multiple basal liners, the above information may either be condensed into an overall summary of the assumed effectiveness of the basal lining or presented for each layer and
* A summary of the physical nature and attenuating properties of the unsaturated zone below each landfill cell:
  + - * Names and mineralogies of the geological formations.
      * Maximum and minimum thickness.
      * Hydraulic conductivity descriptive statistics (estimated and / or measured).
      * Cation exchange capacity descriptive statistics (estimated and / or measured).
      * Descriptive statistics for any other attenuating properties used for design purposes.
      * Maximum acceptable and predicted actual leakage rate.
      * Assumed overall attenuation factor for specific determinands assumed in site design and
      * Estimated travel time through the unsaturated zone.

### Catchment details

A summary of the main hydrological and hydrogeological information for the catchment area should be provided. The following is a checklist of information which, if relevant for the site, should either appear in the risk-based monitoring review or be readily available and clearly referenced:

* Climatic data[[6]](#footnote-6):
  + - * Mean annual rainfall and
      * Effective rainfall (e.g. for bare soil and restoration surface).
* Groundwater data (for each separate groundwater system identified):
  + - * Name of geological formation.
      * Groundwater vulnerability.
      * Existing water quality, and regulatory standards applicable to the groundwater system (e.g. potable water quality)and the groundwater control and trigger levels derived for the site.
      * Abstractions.
      * Total area of the defined groundwater catchment area(s) up and downgradient of the site.
      * Maximum and minimum thickness of saturated zone below site.
      * Groundwater flow direction.
      * Hydraulic gradient.
      * Maximum and minimum thickness of saturated strata within defined catchment area(s).
      * Assumed mixing depth below site.
      * Hydraulic conductivity (estimated or measured).
      * Effective porosity (estimated or measured).
      * Maximum and minimum width of flow below site.
      * Volume of groundwater flow available for dilution as used in design calculations.
      * Groundwater flow velocity (estimated or measured).
      * Assumed or measured attenuating properties used for design purposes; and
      * groundwater discharges.
* Surface water data (for each separate identifiable water course):
  + - * Name of surface water body.
      * Surface water system (i.e. ‘tributary of River x’, ‘part of y catchment).
      * Existing water quality and water quality classification.
      * Water quality objective or other regulatory standards applicable (e.g. environmental quality standards, class limits, drinking water quality) and any compliance levels or assessment criteria derived for the site.
      * Abstractions.
      * Riparian ownership and rights.
      * Conservation status or amenity value and
      * Stream flow statistics (low (Q95 or Q90)[[7]](#footnote-7) and median flow rates at specified locations)[[8]](#footnote-8).

### Risk inventory

In order to prioritise risks for monitoring purposes, the probability that leachate will impact each specific receptor via an identifiable pathway should be evaluated. This information should be summarised in the form of a risk inventory. The risk inventory should itemise each receptor and potential contaminant pathway and indicate how this might be monitored. An example of how information may be arranged is provided as Table 4.2. This particular example is grouped by receptors, since the risks to these are more easily categorised. Alternative arrangement of information may be more suited to other sites, as long as all potential leachate escape routes to receptors are identified for monitoring purposes. The generalised examples given in Table 4.2 are by no means comprehensive and should be replaced by site-specific details.

The risk inventory provides a convenient summary of information assessed when designing the risk-based monitoring plan. It should be incorporated into the site environmental management or monitoring plan to focus the design of the overall monitoring strategy for the site. The inventory will be used to specify the monitoring objectives, which are described in the following chapter (Section 5.4.1).

**Table 4.2: EXAMPLES of issues to be summarised in a risk inventory to aid monitoring programme design for a landfill site**

| **Water receptor at risk**  **Description** | **Water receptor at risk**  **Vulnerability1** | **Contaminant Source**  **Mechanism** | **Possible Pathway**  **Description** | **Possible Pathway**  **Travel time** | **Possible Pathway**  **Mitigation** | **Monitoring Priority**  **Measurements** | **Monitoring Priority**  **Risk2** | **Possible Monitoring Locations** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Groundwater below and down-gradient of site | Dependent on aquifer | Below ground seepage of leachate | Containment system  Unsaturated zone  Groundwater flow | Dependent on presence or absence of each pathway and flow mechanisms | Travel time relative to attenuation3 rates | List I and II and other appropriate quality standards | \* | Leakage detection layer  Unsaturated zone monitoring (e.g. resistivity array)  Boreholes on down-gradient site boundary |
| Groundwater abstraction | Dependent on abstraction use | Below ground seepage of leachate | Containment system  Unsaturated zone  Groundwater flow | Dependent on presence or absence of each pathway and flow mechanisms  Direction and distance to abstraction | Attenuation properties  Travel time | Water quality standards relevant to abstraction | \* | Leakage detection layer  Unsaturated zone monitoring (e.g. resistivity array)  Boreholes on down-gradient site boundary  Borehole(s) on pathway  Abstraction point |
| Stream in catchment area | Dependent on EQS4 and flow conditions | Surface leachate seepages and run-off | Overland run-off  Run-off via ditches and field drains | Rapid particularly following heavy rainfall | Interceptor ditches  Settlement lagoons | Suspended solids  EQS for surface water | \* | Known seepages  Interception points  Receiving water course |
| Stream in catchment area | Dependent on EQS4 and flow conditions | Leachate treatment or storage plant | Consented discharges  Accidental discharges | Immediate | Automated monitoring  Engineered safety controls | Determinands required by consent conditions | \* | Discharge point  Receiving water course |
| Stream in catchment area | Dependent on EQS4 and flow conditions | Below ground seepage of leachate | Containment system  Unsaturated zone  Groundwater flow | Dependent on presence or absence of each pathway and flow mechanisms | Travel time relative to attenuation3 rates | EQS for surface water | \* | Leakage detection layer  Unsaturated zone monitoring (e.g. resistivity array)  Boreholes on down-gradient site boundary  Borehole(s) on pathway  Receiving water course (in high risk situations) |
| Surface water abstraction, conservation or amenity feature | Dependent on use | All of above | All of above plus Surface water flow | All of above | All of above | Appropriate standards for receptor | \* | All of above |

1 Vulnerability refers to seriousness of impact if it did occur, and not to the probability of impact.

2 Risk classification is site-specific and dependent on source (leachate quality), travel time, attenuation factors and receptor vulnerability. \* Risk classification should be quantitative, ranked or qualitative (e.g. ‘insignificant’, ‘low’, ‘medium’, ‘high’), according to circumstances.

3 Attenuation mechanisms primarily include dilution, retardation and biodegradation.

4 EQS: Environmental quality standa4rd for surface water.

# Part 2: The Site Control and Monitoring Plan

# Design Issues and Monitoring Objectives

## Introduction

The remaining chapters of this guidance describe the process of designing a programme of monitoring for landfill leachate impact and specifying this information within a site control and monitoring plan. This plan may also incorporate elements of other monitoring programmes at the site, which are the subject of other guidance (e.g. gas monitoring).

The site control and monitoring plan will provide the principal information source regarding site monitoring throughout its permitted lifetime. For non-inert sites, this is likely to be a considerable number of years after the site has ceased to operate. This document will become the principal technical reference for monitoring at the site and should therefore provide information about the key elements of the site and surrounding area relevant to the ongoing monitoring programmes.

Production of the site control and monitoring plan is an iterative process. Periodic review against monitoring objectives is necessary in the light of monitoring results, changes in technology, legislation and technical guidance.

Guidance is given in this chapter as follows:

* Section 5.2: outlines the issues to be addressed when designing site control and monitoring programmes and preparing the content of the site monitoring or environmental management plan.
* Section 5.3: highlights the need for technical competence and the use of a wide skill base for different monitoring tasks and
* Section 5.4: provides example specifications of monitoring objectives. These form the framework around which the site monitoring or environmental management plan should be formulated.

## Introduction

### Division of contents

The site control and monitoring plan should include:

* Monitoring objectives (both risk-based and legislative), design details and procedures to be adopted for site monitoring and
* Information and data needed to understand and interpret monitoring information.

### Specifications within the site monitoring plan

The site monitoring plan should incorporate specifications to include the following issues:

1. Management structure and technical competence (Section 5.3).
2. Monitoring objectives (Section 5.4).
3. The number and location of monitoring points (Section 6.2).
4. Monitoring measurements (Section 6.3).
5. Monitoring schedules (Section 6.4).
6. Assessment criteria (control and trigger levels) and contingency actions (Chapter 7).
7. Design of monitoring points (Chapter 8).
8. Monitoring methodology (Chapter 9).
9. Data management and reporting procedures (Chapter 10) and
10. Quality assurance (Section 10.3) including quality control measures for items 7, 8 and 9 above.

Some of the above issues will need to be considered simultaneously, though the sequence given is recommended in order to fully address all monitoring issues.

### Technical appendices

Technical reference information needed for monitoring programmes should ideally be collated into a digestible format within the site control and monitoring plan for reference by site monitoring personnel and SEPA. Where such data have been comprehensively collated for other purposes (e.g. in a hydrogeological risk assessment) cross-referencing to these sources may be acceptable.

The objective of collating information is to provide in one single, updateable document all necessary information for monitoring including: summary of risk-based monitoring strategy; monitoring infrastructure details; sampling protocols; and baseline data summaries.

## Management and technical competence

### Management of monitoring plans

The site control and monitoring plan should identify the person responsible and the management structure in place for delivery of the plan. This should include the mechanisms for liaison between the different people involved and with SEPA.

### Technical competence

EASR permit conditions are unlikely to be issued which specify technical skills or qualifications for monitoring personnel. However, permit conditions may specify the need for appropriate Quality Assurance and Control systems, which necessitate the use of appropriately qualified and technically competent staff.

Monitoring is a multidisciplinary scientific activity requiring a variety of inter-related managerial and technical skills. Whilst many routine tasks can be undertaken by personnel with a basic scientific background, there will usually be a need for appropriate training in monitoring and quality control procedures to reinforce this basic knowledge. Depending on the complexity of the monitoring regime, there may be a need during the development and implementation of a monitoring programme for the involvement of a number of different personnel with specific technical competencies. Examples of specialist skill areas are illustrated in Table 5.1.

### Training

Training of personnel should follow standards established by bodies such as the Waste Management Industry Training and Advisory Board (WAMITAB). Attendance on specialist short courses undertaken by recognised training bodies should be encouraged and reinforced by in-house training by supervisory staff. All monitoring personnel should be encouraged to be members of professional institutions and to keep their professional accreditation up to date by participation in continuous professional development (CPD) programmes.

The use of inexperienced personnel on monitoring programmes without prior training is not acceptable. Training records of monitoring personnel (whether sourced from in-house or from sub-contractors or consultants) should be made available to SEPA on request.

## Monitoring objectives

### Specification and grouping of objectives

Site-specific monitoring objectives should be listed in the site control and monitoring plan. These should be unambiguous, practically achievable, and form the principles for monitoring on which all subsequent sections of the site control and monitoring plan should rely. Objectives should be periodically reviewed, particularly in situations where changes to the site design occur or external influences impact on the surrounding water environment.

For any given site, objectives should be set which meet the specific risks set out in the risk inventory (Chapter 4). Each objective should clearly state the risk that is to be monitored and the method of measurement.

Example monitoring objectives are given in this chapter. Objectives are sub-divided under the following headings related to the monitoring programmes defined in Section 3.7, but include additional issues, such as non-leachate related sources of contamination and water balance:

* Objectives for monitoring landfill leachate (leachate characterisation monitoring).
* Objectives for monitoring of other contaminant sources within the landfill area.
* Objectives for initial characterisation monitoring of groundwater and surface water.
* Objectives for routine monitoring of groundwater and surface water and
* Objectives for site water balance monitoring.

#### Table 5.1: EXAMPLES of the possible range of technical skills needed for a monitoring programme

**Table 5.1a: Management**

| **Tasks** | **Programme Co-ordination** | **Quality Control** | **Liaison with EA** | **Liaison with sub-contractors / laboratory** |
| --- | --- | --- | --- | --- |
| Routine |  |  |  | \* |
| Specialist: Monitoring Manager1 |  |  |  |  |
| Specialist (Supporting): Hydrogeology |  | \* |  | \* |
| Specialist (Supporting): Landfill Engineering |  | \* |  |  |
| Specialist (Supporting): Chemistry |  | \* |  | \* |
| Specialist (Supporting): Hydrology |  | \* |  |  |
| Specialist (Supporting): Biology |  | \* |  | \* |
| Specialist (Supporting): Database / IT |  | \* |  | \* |
| Specialist (Supporting): Mathematics / Statistics |  | \* |  |  |

1 The Monitoring Manager should be a competent professional with a specialism in at least one of the supporting disciplines.

Indicates the primary specialist skills needed for a specific monitoring activity.

\* Indicates additional skill areas where advice may be needed for a specific monitoring activity.

**Table 5.1b: Risk Assessment and Specification of Monitoring Programmes**

| **Tasks** | **risk-based Monitoring Assessment** | **Monitoring Objectives** | **Monitoring Schedules** | **Design of Compliance / Trigger Tests** | **Contingency Planning** | **Monitoring Protocols** |
| --- | --- | --- | --- | --- | --- | --- |
| Routine |  |  |  |  |  | \* |
| Specialist: Monitoring Manager1 | \* | \* | \* | \* | \* | \* |
| Specialist (Supporting): Hydrogeology |  |  |  |  | \* |  |
| Specialist (Supporting): Landfill Engineering |  |  |  |  |  |  |
| Specialist (Supporting): Chemistry | \* | \* | \* | \* |  |  |
| Specialist (Supporting): Hydrology | \* | \* | \* | \* | \* |  |
| Specialist (Supporting): Biology | \* | \* | \* | \* |  |  |
| Specialist (Supporting): Database / IT | \* |  |  |  |  |  |
| Specialist (Supporting): Mathematics / Statistics | \* | \* |  |  |  |  |

1 The Monitoring Manager should be a competent professional with a specialism in at least one of the supporting disciplines.

Indicates the primary specialist skills needed for a specific monitoring activity.

\* Indicates additional skill areas where advice may be needed for a specific monitoring activity.

**Table 5.1c: Design and Certification of Monitoring Infrastructure**

| **Tasks** | **Leachate** | **Groundwater** | **Surface water** |
| --- | --- | --- | --- |
| Routine |  |  |  |
| Specialist: Monitoring Manager1 | \* | \* | \* |
| Specialist (Supporting): Hydrogeology | \* |  |  |
| Specialist (Supporting): Landfill Engineering |  |  |  |
| Specialist (Supporting): Chemistry |  |  |  |
| Specialist (Supporting): Hydrology |  |  |  |
| Specialist (Supporting): Biology |  |  | \* |
| Specialist (Supporting): Database / IT |  |  |  |
| Specialist (Supporting): Mathematics / Statistics |  |  |  |

1 The Monitoring Manager should be a competent professional with a specialism in at least one of the supporting disciplines.

Indicates the primary specialist skills needed for a specific monitoring activity.

\* Indicates additional skill areas where advice may be needed for a specific monitoring activity.

**Table 5.1d: Field Surveys**

| **Tasks** | **Routine Monitoring Surveys** | **Biological Sampling** | **Volatile Organic Sampling** |
| --- | --- | --- | --- |
| Routine |  | \* | \* |
| Specialist: Monitoring Manager1 | \* | \* | \* |
| Specialist (Supporting): Hydrogeology |  |  | \* |
| Specialist (Supporting): Landfill Engineering |  |  |  |
| Specialist (Supporting): Chemistry |  |  |  |
| Specialist (Supporting): Hydrology |  |  | \* |
| Specialist (Supporting): Biology |  |  |  |
| Specialist (Supporting): Database / IT |  |  |  |
| Specialist (Supporting): Mathematics / Statistics |  |  |  |

1 The Monitoring Manager should be a competent professional with a specialism in at least one of the supporting disciplines.

Indicates the primary specialist skills needed for a specific monitoring activity.

\* Indicates additional skill areas where advice may be needed for a specific monitoring activity.

**Table 5.1e: Data Collation, Interpretation and Reporting**

| **Tasks** | **Data Collation** | **Data Validation** | **Data Review and Interpretation** | **Reporting** |
| --- | --- | --- | --- | --- |
| Routine |  |  | \* | \* |
| Specialist: Monitoring Manager1 | \* | \* |  |  |
| Specialist (Supporting): Hydrogeology | \* | \* | \* | \* |
| Specialist (Supporting): Landfill Engineering | \* |  |  | \* |
| Specialist (Supporting): Chemistry | \* | \* | \* | \* |
| Specialist (Supporting): Hydrology | \* | \* | \* | \* |
| Specialist (Supporting): Biology | \* | \* | \* | \* |
| Specialist (Supporting): Database / IT | \* | \* | \* | \* |
| Specialist (Supporting): Mathematics / Statistics | \* | \* | \* | \* |

1 The Monitoring Manager should be a competent professional with a specialism in at least one of the supporting disciplines.

Indicates the primary specialist skills needed for a specific monitoring activity.

\* Indicates additional skill areas where advice may be needed for a specific monitoring activity.

The example objectives given in this chapter should not generally be quoted verbatim in the site control and monitoring plan but should be used as a guide for developing site-specific objectives. For example, a number of groundwater objectives may be needed to address the risks associated with the potential for contamination of individual receptors. The example objectives have been developed with biodegradable landfill sites in mind and modifications would be necessary for any other type of landfill. In general, sites that pose high risks will require additional objectives. Sites with low risks may be served by lesser objectives.

### Objectives for monitoring landfill leachate

Objective 1: To determine the level of leachate within the landfill:

* 1. To determine the head of leachate on the base of the site in each landfill cell to determine the effectiveness of leachate management and extraction systems in complying with design and regulatory maximum levels.
  2. To determine the level of leachate adjacent to the site boundary to monitor compliance with design and regulatory maximum levels and to provide early warning of the potential for overspill of leachate to surface waters or the potential for lateral seepages into groundwater.
  3. To determine leachate levels for the purpose of improving estimates of leachate volumes within the site to assist in the design, operation and maintenance of leachate management systems and
  4. To determine leachate levels for comparison with design assumptions of levels used in calculations of potential basal and lateral seepage rates.

If any of the above objectives cannot be achieved and the risk to the water environment is significant, increased monitoring of groundwater and surface waters will usually be required.

Objective 2: To determine the quality of leachate and its variation in space and time within the body of the landfill:

1. To identify specific chemical characteristics of leachate that may help in unambiguously identifying leakage into groundwater and surface water.
2. To provide information on the state and rate of stabilisation of the waste body for comparison with the design lifetime of the containment and monitoring systems and to assist with the demonstration that the site no longer poses a hazard to the environment for application to surrender a permit or licence.
3. To determine the presence of harmful substances in leachates in relation to the risk at defined receptors (e.g. the presence of List I or List II substances in leachate should be used to guide the monitoring programme for groundwater under The Groundwater Regulations 1998) and
4. To determine the quality of leachate for direct discharge to a treatment system.

Objective 3: To determine the level, flow and quality of leachate and its variation in time, in surface storage and treatment systems:

1. To determine the level of leachate in a storage lagoon in relation to overflow maxima.
2. To determine the volume of leachate discharged from storage or treatment systems and
3. To identify specific chemical characteristics of leachate that are required to support a consented discharge from storage lagoons and / or treatment systems.

### Objectives for monitoring of other contaminant sources within the landfill area

Objective 4: To provide quality assurance that other sources of potential water contamination within the landfill site are controlled as designed:

1. To detect any spillage of fuel from fuel stores/ bunded areas.
2. To detect any spillage of contaminated water from wheel washers and other cleaning areas.
3. To detect any spillages from chemical storage areas, waste transfer areas or waste processing areas of any type and
4. To detect any poorly controlled run-off from landfill areas that may carry suspended solids or contamination.

Many of the above issues are covered by standard planning and permit conditions. Where good engineering controls are in place, monitoring may simply be based on observational records. Provision of specific monitoring points and sampling will only be required where leakage is threatened or is present, particularly from non-engineered or poorly engineered facilities.

Objective 5: To provide monitoring information required by the terms of a surface water discharge consent such as water quality and flow measurements as specified in a consent to discharge to surface water.

Monitoring of discharges by the operator may be specified in the consent or permit and it is recommended that details are included in the site control and monitoring plan.

### Objectives for initial characterisation monitoring of groundwater and surface water

For new sites, initial characterisation monitoring programmes should be initiated at least one year in advance of site development (see Section 6.4.2 for further detail on initial groundwater and surface water monitoring). For older sites with inadequate monitoring records, initial characterisation monitoring programmes may be introduced retrospectively and should be undertaken in conjunction with assessment of any historical or other relevant data.

Objective 6: To characterise the underlying and surrounding groundwater systems for future comparison against any landfill impacts and to determine compliance and assessment limits where appropriate:

1. To determine initial baseline groundwater level including variability and trends and
2. To determine initial baseline groundwater quality including variability and trends.

Objective 7: To characterise surface water quality and level and/or flow for future comparison against any landfill impacts and to determine compliance and assessment limits where appropriate:

1. To determine initial baseline water quality of surface waters, including variability and trends.
2. To determine initial baseline stream flow (where required for dilution calculations), including variability and trends and
3. To determine initial baseline water level in surface water bodies (where required for hydrological assessment), including variability and trends.

### Objectives for routine monitoring of groundwater and surface water

Once initial characterisation monitoring has been completed, routine monitoring should form the normal pattern of monitoring.

Objective 8: To carry out routine monitoring of groundwater to provide ongoing baseline data, and to discern deviations from baseline conditions:

1. To carry out routine monitoring of groundwater level and
2. To carry out routine monitoring of groundwater quality and determine if there have been any breaches in control or trigger levels.

Objective 9: To carry out routine monitoring of surface water to provide ongoing baseline data, and to discern deviations from baseline conditions:

1. To carry out routine monitoring of surface water level or flow and
2. To carry out routine monitoring of surface water quality and determine if there have been any breaches in assessment or compliance levels.

### Objectives for site water balance monitoring

Objective 10: To quantify water inputs and outputs within the site:

1. To determine natural water input from rainfall.
2. To determine the volume of liquid added to each hydraulically separate landfill cell.
3. To determine the volume of leachate removed from each hydraulically separate landfill cell and
4. To determine the total volume of leachate discharged off-site.

# Monitoring Locations and Schedules

## Introduction

Monitoring at landfill sites should be risk-based while taking in account the minimum monitoring requirements of the Landfill Regulations. In a risk-based design process, existing monitoring schedules and infrastructure should be completely re-appraised. Monitoring locations and schedules (the subject of this chapter) should be considered before infrastructure and sampling strategies are designed (Chapters 8 and 9). This process may lead to the provision of new monitoring points and/or the redesign or removal of existing monitoring points as well as revision of schedules.

In this chapter, a series of example monitoring schedules are presented. However, the use of a risk-based methodology for designing monitoring programmes may lead to instances where monitoring measurements and frequencies are proposed which vary from those provided in the model schedules. For example, lesser requirements may be justifiable for sites posing low risks to receptors. Conversely, greater requirements may be needed for sites accepting potentially polluting waste types where risks are considered to be more vulnerable.

Guidance is given in this chapter as follows:

* Section 6.2: the number and location of monitoring points.
* Section 6.3: monitoring measurements typically carried out at landfill sites and
* Section 6.4: specification of monitoring schedules for different monitoring programmes.

## The number and location of monitoring points

### Preamble

This section provides general guidance on the minimum number and locations of monitoring points required for leachate, groundwater and surface water monitoring. When selecting monitoring locations, it is important to be aware of the purpose of monitoring, as defined in the monitoring objectives and the risk-based monitoring assessment. In addition, monitoring also need to comply with the minimum requirements of the Landfill Directive.

Examples summarising a monitoring point assessment for sites in low and high-risk settings are presented as Tables 6.1 and 6.2

### Number and location of leachate monitoring points

The location of monitoring points in relation to leachate drainage systems and collection sumps should be chosen carefully. Leachate levels need to be representative of levels across the landfill as a whole and not artificially lowered by proximity to a dewatering point.

Schedule 4 of the Landfill Regulations specifies the following monitoring requirements:

* Samples of leachate or surface water (if present) must be collected at representative points.
* Sampling and measuring of the volume and composition) of any leachate must be performed separately at each point at which leachate is discharged from the site and
* A sample of leachate and water representative of the average composition shall be taken for monitoring purposes in accordance with Table 1. This table details the frequency of leachate monitoring.

To comply with the above requirements and to undertake the leachate monitoring in a risk-based manner the following guidance should be followed:

* Leachate levels and quality samples can be obtained from the same or separate monitoring points as long as the monitoring objectives can be achieved. For example, samples could be taken from underdrainage or dewatering points, with levels obtained independently from other monitoring points remote from the point of leachate removal.
* Where leachate can be shown to drain freely through the waste and can be removed via a basal drainage system, a sample of the drained leachate will be acceptable as appropriate for leachate quality at the site base.
* To obtain representative samples of leachate, samples should be collected from abstraction points prior to undergoing any treatment.

**Table 6.1: EXAMPLE summary of monitoring point assessment for a site posing a low risk to water receptors**

| **Monitoring Location** | **Purpose** | **Type of monitoring point** | **Number and spacing of monitoring points** |
| --- | --- | --- | --- |
| Groundwater on site boundary1 | To assess quality and levels | Boreholes | 1 up-gradient and 2 down-gradient per groundwater system |
| Surface water at suspended solids in run-off | Impact on quality from downstream of each outfall | Surface water | At least 1 point upstream and 1 point outfall from site |

1 Unless reliable waste input and/or leachate monitoring is established which demonstrates unambiguously that polluting, leachate is not being produced. However, groundwater control and trigger levels still need to be derived.

* Where perched leachate levels are developed and/or hydraulic continuity in landfill cells is poor[[9]](#footnote-9), the number of sample points should be based on that recommended in Table 6.3.
* At least two leachate level monitoring points in addition to a collection sump should be provided for each hydraulically separated cell of less than 5 ha in size. For larger cell sizes, the guidance in Table 6.3 should be followed. These points should be capable of recording the level of leachate in relation to the base of the site.

Level monitoring points should include points remote from leachate drainage and pumping systems. Sumps or boreholes designated for level monitoring which are frequently pumped should be tested to determine the time of recovery to rest water level. Levels should be taken from these points after pumps are switched off and sufficient time to obtain a reliable rest water level has passed. Where this cannot be achieved a level reading can still be taken but a record of pumping activity should be made and

* Additional monitoring points and controls may be needed where leachate levels (perched or otherwise) cannot be controlled adequately, particularly where there is a threat or incidence of overspill to surface or of lateral seepage to groundwater.

**Table 6.2: EXAMPLE summary of monitoring point assessment for a biodegradable site posing a moderate to high risk to water receptors**

| **Monitoring Location** | **Purpose** | **Type of monitoring point** | **Typical number of monitoring points** |
| --- | --- | --- | --- |
| Landfill cells | Leachate level and quality at base of site or within waste mass  Leachate quality in underdrainage layer (site base) | Sumps, boreholes  Drainage collection point | 2 level monitoring points per 5 ha1 cell in addition to a leachate extraction point  1 appropriate quality point per 5 ha cell. Level monitoring points as above |
| Leakage detection layer | To determine leakage | Drainage collection point | At least 1 per 5 ha cell |
| Electrical resistivity array in unsaturated zone | To determine leakage | Resistivity array | Suitably designed and extensive electrode array2 |
| Groundwater on site boundary | Quality and levels to be monitored for comparison to assessment criteria (e.g. control and trigger levels).  To monitor compliance with the Groundwater Regulations 1988 | Boreholes | A minimum of 1 up-gradient and 2 down-gradient per groundwater system  Spaced a maximum of 100m apart on down-gradient boundary |
| Groundwater between site and receptors at risk | Potential impact on quality in down-gradient water abstraction well and surface water course | Boreholes | At least one for each receptor and/or pathway(s) connecting the landfill and the receptor(s) |
| Surface water at outfall from site | Impact on surface water quality | Surface water | At least one point upstream and one point downstream of each outfall |

1 1ha = 10,000m2

2 The long-term reliability and durability of resistivity arrays for unsaturated zone monitoring is uncertain.

### Number and location of groundwater monitoring points

Groundwater monitoring should be carried out in a risk-based manner although the minimum requirements of the Landfill Regulations must also be met. The Landfill Regulations specify that for groundwater:

* The sampling measurements must be sufficient to provide information on groundwater likely to be affected by the discharge from the landfill, with at least one measuring point in the groundwater inflow region and two in the outflow region.
* The number of measurements may be increased on the basis of a specific hydrogeological survey on the need for an early identification of accidental leachate release in the groundwater and
* Sampling must be carried out in at least three locations before the filling operations in order to establish reference values for future sampling.

**Table 6.3: Minimum number of leachate monitoring points**

| **Site Area (ha)1**  **from** | **Site Area (ha)1**  **to** | **Number of Monitoring Points2** |
| --- | --- | --- |
| 0+ | 5 | 3 |
| 5+ | 10 | 4 |
| 10+ | 25 | 6 |
| 25+ | 50 | 9 |
| 50+ | 75 | 11 |
| 75+ | 100 | 13 |
| 100+ | 125 | 15 |
| 125+ | 150 | 16 |
| 150+ | 175 | 17 |
| 175+ | 200 | 18 |
| 200+ | 250 | 19 |
| 250+ | And upwards | 20 |

Table details taken from Waste Management Paper 26A, Table 3.1

1 For landfills operated in a phased, cellular manner with hydraulically isolated leachate collection systems, the area referred to in the table shall be that of each cell.

2 At least two monitoring points in each cell should be situated away from the point of leachate discharge.

The number and location of monitoring points should follow on from risk assessment. However, the following guidance gives some recommendations which could be followed when determining the minimum number and location of groundwater monitoring points:

* For engineered containment sites where any leakage of leachate is likely to be diffuse (e.g. by use of mineral liners), at least one borehole should be provided per 100 metres width of site on the down-gradient landfill site margin. These should be located as close as possible to edge of the landfill but for practical purposes should be no closer than 10 metres and no further than 100 metres from the waste margin.
* For engineered sites in which leakage could potentially occur from holes or tears over a restricted area (e.g. by use of artificial sheet liners) or sites located above fissured strata and in which a leachate detection layer is absent or non-operational, at least one borehole should be provided per 50 metres width of the down-gradient landfill site margin. These should be located as close as possible to edge of the landfill but for practical purposes should be no closer than 10 metres[[10]](#footnote-10) and no further than 100 metres from the waste margin.
* Any plausible pathways between the landfill site and a water receptor should be intercepted by at least one monitoring point, which may be additional to the boreholes on the site boundary. For more sensitive receptors, where flowpaths are uncertain, more than one monitoring point is likely to be required and
* For the highest risk sites additional remote monitoring schemes may be appropriate (e.g. resistivity arrays installed within an unsaturated zone below the landfill site). Where these are deployed, they should be proven to be operationally reliable over a period of several years following construction of the overlying landfill.

In selecting monitoring locations, consideration should be given to choosing points:

* Where the pathway is well understood, in order to minimise uncertainty and
* As close as possible to the leachate source (but no closer than 10 m from the edge of a landfilled area), in order to provide an early warning of leachate migration.

It may not always be possible to satisfactorily meet both these requirements at one location, in which case additional monitoring points will be required.

Monitoring requirements (in terms of numbers and location) can increase in complexity as monitoring progresses, particularly if leachate contamination is detected resulting in a requirement for assessment monitoring.

In many cases, groundwater monitoring locations will be needed outside the licensed area of operations and on land outside the ownership of the site operator. Necessary permissions to access this land and to maintain access for monitoring purposes are vital[[11]](#footnote-11).

The separation distance between groundwater monitoring points is site-specific and should be justified by the risk-based monitoring review. For this reason, the monitoring may be varied from that stated above. The vertical positioning of monitoring points can also be an issue and requires a good conceptual knowledge of geological and hydrogeological conditions at a site. For example, a contamination “plume” may develop which sinks below the water table as it progresses further down-gradient from the site. Factors such as the amount of rainfall recharge, gravitational settlement, and hydrodynamic dispersion can all influence the vertical component of contaminant transport in groundwater.

### Number and location of surface water monitoring points

Surface water monitoring should also be risk-based but should take account of the requirements of the Landfill Regulations which specifies that:

* Sampling of surface water if present must be collected at representative points and
* Monitoring of surface water if present shall be carried out at not less than two points, one upstream and one downstream.

However, this is a minimum requirement and may be increased following risk assessment. In determining the number of surface water monitoring points required at a site, it is recommended that the following guidelines be followed although these recommendations can be relaxed if justified by risk assessment:

* For surface waters which are sensitive to small changes in water quality (e.g. wetlands), at least two upstream and two downstream monitoring points are required and
* At least one monitoring point is required for each area of ponded water, wetland or lake located within the site boundaries or within the downgradient catchment area of the site where these are potentially at risk. Additional monitoring points may be required in relation to risk.

The distance between surface water monitoring points in a flowing water course is site specific.

In many cases, surface water monitoring locations will be needed outside the licensed area of operations and on land outside the ownership of the site operator. It is essential that the necessary permissions to access this land and to maintain access for monitoring purposes are obtained[[12]](#footnote-12).

## Introduction

The site monitoring plan should include tables specifying:

* Monitoring measurements to be undertaken.
* The units of measurement.
* The tolerable uncertainty.
* The detection limit (where appropriate) and
* The analytical method.

Again, the selection of monitoring measurements should be risk-based and will be related to the characteristics of the leachate and the surrounding groundwater and surface water. Initially this would relate to the waste types deposited (e.g. from obtaining leachate quality from a similar type of landfill taking similar waste streams) until leachate generation and monitoring has begun. The final choice of measurements is site specific, and subject to the results of the risk-based monitoring review. Periodic review of the selection of monitoring measurements should be undertaken.

However, it also has to take into the account the monitoring requirements of the Landfill

Regulations which states that:

* For groundwater, the parameters to be analysed must be derived from the expected composition of the leachate and the groundwater quality in the area. In addition, in selecting the parameters for analysis the mobility in the groundwater zone must be taken into account. Parameters may include indicator parameters in order to ensure an early recognition of changes in water quality. Recommended parameters include, pH, TOC, phenols, heavy metals, fluoride, As and oil/hydrocarbons and
* For leachate the Directive states that the parameters to be measured and the substances to be analysed vary according to the composition of the waste deposited; they must be specified in the conditions of the landfill permit and reflect the leaching characteristics of the wastes.

Initial and ongoing characterisation monitoring programmes encompass a broad suite of measurements to determine identifying characteristics of leachate, groundwater and surface water. After initial characterisation is complete, a range of indicator measurements may be selected for use in routine monitoring programmes.

Monitoring measurements can be sub-divided into the following broad categories:

* Observational and physical measurements.
* Principle chemical composition measurements.
* Minor chemical composition measurements and
* Biological measurements.

Toxicity measurements, which are increasingly in use for sewage detection, may in future become more important for monitoring purposes. These are at an early stage of development for leachate monitoring and are therefore not covered in any detail by this guidance document.

The above categories of measurement are discussed in the following sections.

### Observational and physical measurements

These include:

* Simple observations which can be recorded into a log book or by photography (e.g. surface seepages of leachate).
* Measurements which can be undertaken with simple field equipment (e.g. water levels) and
* Measurements which can be automated or estimated (e.g. leachate discharge volumes).

Examples of typical observational and physical measurements used in monitoring programmes are provided in Table 6.4.

### Principal chemical composition measurements

These include the main chemical constituents typical of leachate (which as far as possible should be based on site-specific leachate analysis) and natural waters including physicochemical indicators and major ions, which account for the majority of dissolved minerals in water (Table 6.5).

**Major ion balance**

Where a sufficient number of major ions are analysed (see Table 6.5), a major ion balance should be routinely undertaken and reported by the analytical laboratory as part of normal laboratory quality control procedures.

The difference between analysed cations and anions can be expressed either as a percentage of total cations, or anions, or the sum of both. To standardise the approach for monitoring purposes the following formula should be used:

Percentage difference = Sum of cations (meq/l) minus Sum of anions (meq/l) over Sum of cations (meq/l) plus Sum of anions (meq/l) times 100

Cations (positively charged) and anions (negatively charged) are identified in Table 6.5. Cations and anions are expressed in units of milliequivalents per litre (meq/l). Conversion factors from mg/litre to milliequivalents per litre are provided in Appendix 13.

The use of quality control checks, including major ion balance, is described in Section 10.6.

### Minor chemical composition measurements

Minor chemical constituents (Table 6.6) can be subdivided under the following headings:

* Inorganic and organic contaminants, including trace metals. These will vary between waste types.
* Substances or properties, which are harmful at identified receptors These are substances not included in the above or major chemical constituency categories but which may be selected for particular attention in relation to specific receptors and
* Other substances required by regulatory conditions or discharge consent. For example, List I and List II substances in relation to discharges to groundwater; Red List substances and dissolved methane in relation to discharges to sewer or surface water.

### Biological measurements

If required by risk assessment, biological measurements may include the identification of specific organisms in relation to impact on water resources (e.g. analysis of coliform bacteria in relation to impact on potable water supplies) or indicator measures of biotic communities (which can be used to classify the quality of stream water).

Examples of biological measurements are provided in Table 6.7.

**Table 6.4: Description of example observational and physical monitoring measurements**

**Table 6.4a: Observational Measurements**

| **Measurement** | **Specification** | **Units** | **Tolerable uncertainty** |
| --- | --- | --- | --- |
| Observation of landfill run-off | Weekly / monthly logged observation of site conditions during and following rainfall. | n/a1 | (4) |
| Observation of other contaminant sources | Weekly / monthly logged observation of drainage arising from other contaminant sources. | n/a | (4) |
| Observation of vegetation | Weekly / monthly logged observations of vegetation die-back | n/a | (4) |

1 n/a: not applicable.

(4) The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site and measurement specific (see Section 6.3.5).

**Table 6.4b: Water Balance Measurements**

| **Measurement** | **Specification** | **Units** | **Tolerable uncertainty** |
| --- | --- | --- | --- |
| Rainfall | Annual and monthly total and effective rainfall | mm | (4) |
| Volume removed2 | Volume of leachate removed from each cell by drainage or pumping | m3 per unit of time | (4) |
| Volume added2 | Volume of leachate or other fluids added onto or into each landfill cell | m3 per unit of time | (4) |
| Volume discharged2 | Volume of leachate removed from off-site | m3 | (4) |

2 Typically, data should be summarised into monthly totals collated from daily or more frequent records.

(4) The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site and measurement specific (see Section 6.3.5).

**Table 6.4c: Surface Water Flow Measurements**

| **Measurement** | **Specification** | **Units** | **Tolerable uncertainty** |
| --- | --- | --- | --- |
| Surface water flow | Flow rate | Litre/sec | (4) |

(4) The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site and measurement specific (see Section 6.3.5).

**Table 6.4d: Level Measurements**

| **Measurement** | **Specification** | **Units** | **Tolerable uncertainty** |
| --- | --- | --- | --- |
| Leachate level | Level of liquid in monitoring point recorded by reference to surveyed datum level | m.AOD(3) | (4) |
| Groundwater level | Level of water in monitoring point recorded by reference to surveyed datum level. | m.AOD | (4) |
| Surface water level | Level of water recorded by reference to surveyed datum level | m.AOD | (4) |
| Base of monitoring point | Level of base of monitoring point by reference to surveyed datum level | m.AOD | (4) |

3 m.AOD: metres above ordnance datum

(4) The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site and measurement specific (see Section 6.3.5).

**Table 6.5: EXAMPLES of principle chemical composition measurements**

| **Determinand** | **Symbol** | **Units** | **Field / Lab1** | **Major Ion Balance2** | **Tolerable uncertainty3** |
| --- | --- | --- | --- | --- | --- |
| Temperature5 | Temp | oC | F |  | (3) |
| pH | pH | pH units4 | F and L |  | (3) |
| Electrical conductivity | EC | µS/cm4 | F and L |  | (3) |
| Dissolved oxygen6 | DO | mg/l | F |  | (3) |
| Redox potential6 | Eh | mV | F |  | (3) |
| Total suspended solids | TSS | mg/l | L |  | (3) |
| Total dissolved solids | TDS | mg/l | L |  | (3) |
| Ammoniacal-nitrogen (as N) | NH4-N | mg/l | L | (+) | (3) |
| Total oxidised nitrogen (as N)7 | TON | mg/l | L | (-) | (3) |
| Volatile fatty acids (C2-C5) | VFA | mg/l | L | (+)8 | (3) |
| Total organic carbon (filtered) | TOC | mg/l | L |  | (3) |
| Biochemical oxygen demand | BOD | mg/l | L |  | (3) |
| Chemical oxygen demand | COD | mg/l | L |  | (3) |
| Calcium9 | Ca | mg/l | L | + | (3) |
| Magnesium9 | Mg | mg/l | L | + | (3) |
| Sodium9 | Na | mg/l | L | + | (3) |
| Potassium9 | K | mg/l | L | + | (3) |
| Total alkalinity (as CaCO3) | Alk | mg/l | F or L | - | (3) |
| Sulphate | SO4 | mg/l | L | - | (3) |
| Chloride | Cl | mg/l | L | - | (3) |
| Iron9 | Fe | µg/l | L | (+) | (3) |
| Manganese9 | Mn | µg/l | L | (+) | (3) |

1 Measurements designated “L” would normally be determined at a laboratory, though selected field measurements of indicator parameters may be acceptable to the SEPA subject to agreement of calibration procedures.

2 Determinands marked “+” are cations and “-” are anions used for major ion balance calculation. Bracketed values are those frequently at sufficiently low concentration in natural waters to omit from calculation, but which would normally be included in a major ion balance for leachates.

3 The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site, location and measurement specific (see Section 6.3.5).

4 Typical instrumentation accuracy required, rather than reporting value.

5 Calibration temperature should be stated. Normally this is 20°C.

6 Where DO and Eh measurements are required these should only be determined in the field. Analyses on groundwater samples should only be taken in flow-through cells. Measurements would not normally be carried out on leachate samples.

7 Total oxidised nitrogen may be expressed as the sum of nitrate (NO3) and nitrite (NO2) analyses.

8 If volatile fatty acids are included in a major ion balance, a correction is required for the effect of these acids on the alkalinity value (see Appendix 13).

9 All metals should be dissolved metals unless conditions require total metals (e.g. for surface or ground waters which are fast flowing, or where precipitation of Fe/Mn is occurring in otherwise clear water).

**Table 6.6: Examples of minor chemical composition measurements**

**Table 6.6a: Examples of Inorganic Substances**

| **Determinand1** | **Symbol** | **Units** | **Tolerable uncertainty3** |
| --- | --- | --- | --- |
| Cadmium2 | Cd | µg/l | (3) |
| Chromium2 | Cr | µg/l | (3) |
| Copper2 | Cu | µg/l | (3) |
| Nickel2 | Ni | µg/l | (3) |
| Lead2 | Pb | µg/l | (3) |
| Zinc2 | Zn | µg/l | (3) |
| Orthophosphate (as P) | o-PO4 | µg/l | (3) |
| Arsenic | As | µg/l | (3) |
| Barium | Ba | µg/l | (3) |
| Boron | B | µg/l | (3) |
| Cyanide | CN | µg/l | (3) |
| Fluoride | F | µg/l | (3) |
| Mercury | Hg | µg/l | (3) |
| Dissolved methane | Dis CH4 | µg/l | (3) |

1 All analyses would normally be determined at a laboratory. Field measurements of some determinands may be allowable subject to approval of calibration procedures.

2 All metals should be dissolved metals unless conditions require total metals (e.g. for surface water or groundwater that is fast flowing, or where precipitation of Fe/Mn is occurring in otherwise clear water).

3 The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site, location and measurement specific (see Section 6.3.5).

**Table 6.6b: Examples of Organic Substances**

| **Determinand1** | **Symbol** | **Units** | **Tolerable uncertainty3** |
| --- | --- | --- | --- |
| Phenols (e.g. by HPLC)4 | Mono-P | Mg/l | (3) |
| Mineral Oils5 | Min Oil | µg/l | (3) |
| Pesticides (e.g. Atrazine, Mecoprop) | - | µg/l | (3) |
| Polychlorinated Biphenyls | PCBs | µg/l | (3) |
| Chlorinated Solvents (e.g. Trichloroethylene) | - | µg/l | (3) |

1 All analyses would normally be determined at a laboratory. Field measurements of some determinands may be allowable subject to approval of calibration procedures.

3 The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site, location and measurement specific (see Section 6.3.5).

4 HPLC: High Performance Liquid Chromatography. There are many phenolic compounds. Exact analysis should be specified in consultation between the operator, SEPA and analytical laboratory.

5 Method of mineral oil determination should be specified in consultation between the operator, SEPA and analytical laboratory.

**Table 6.6c: Other Substances Monitored for Regulator Purposes**

| **Determinand1** | **Symbol** | **Units** | **Tolerable uncertainty3** |
| --- | --- | --- | --- |
| Other List I and List II determinands specified by Regulation 15 survey | List I  List II | - | (3) |
| Other Red List/List I determinands for leachate discharge | Red List  List I | - | (3) |

1 All analyses would normally be determined at a laboratory. Field measurements of some determinands may be allowable subject to approval of calibration procedures.

3 The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site, location and measurement specific (see Section 6.3.5).

**Table 6.7: Examples of biological measurements**

| **Biological measurement** | **Description** | **Units / score** | **Tolerable uncertainty5** |
| --- | --- | --- | --- |
| Coliform bacteria | Indicator of faecal contamination | MPN1 index/100ml or no. cfu/100 ml2 | (5) |
| Chlorophyll a | Used to assess the total biomass of algae present. An indicator of nutrient enrichment | mg/m3 | (5) |
| Toxicity tests | Organisms e.g. the microcrustacean Daphnia magna can be exposed to water from the monitoring site to assess the present of toxic conditions. | e.g. 48 hour LC503 | (5) |
| Macroinvertebrate community | Assessment of the species and abundance of benthic macro-invertebrates. | Similarity indices, diversity indices, biotic scores (e.g. BMWP4 and Chandlers Score) | (5) |

1 MPN: Most Probably Number.

2 cfu: Colony Forming Units.

3 LC50: Lethal concentration of a substance, which has a measurable effect on 50% of test organisms within 48 hours.

4 BMWP: Biological Monitoring Working Party score.

5 The tolerable uncertainty would be determined following completion of initial characterisation monitoring and may not necessarily be applied to all measurements. It may be expressed as a percentage or a fixed value. It is site and measurement specific (see Section 6.3.5). For biological and microbiological measurements, uncertainty is generally higher than for chemical or physical measurements.

### Specifying tolerable uncertainty

Tables 6.4 to 6.7 exclude any specification of values or percentage limits relating to the tolerable uncertainty of each monitoring measurement. The tolerable uncertainty should take account of the intended use of the data and should be specified, as a minimum, for those measurements which will be used for routine indicator monitoring and assessment (see 6.4.4 and Chapter 7). Tolerable uncertainty is not only site and measurement specific but may also vary between monitoring points on the same site. Specification of tolerable uncertainty is an iterative process, which should be constantly kept under review throughout the life of a monitoring programme.

Two primary considerations for specifying the tolerable uncertainty of a measurement are:

* The difference in value between baseline and any assessment value to be used (see Chapter 7). Where baseline values are close to assessment limits greater reliability in measurements will be needed (i.e. smaller tolerable uncertainty) and
* The uncertainty that has been achieved in the initial characterisation monitoring.

Where there is a conflict between these two considerations, the uncertainty associated with the initial characterisation monitoring should, wherever possible, be reduced (For example, by using a different analytical method). Where this is impracticable, the assessment limit may need to be changed (see Section 7.3).

For many monitoring measurements, large uncertainties (For example, above 35%) may be acceptable. Where this is the case, there is justification for using less stringent sampling and measurement methods, and collecting a lesser number of samples. Where uncertainties need to be lower, steps should be taken to ensure that methods and sample numbers are appropriate, to ensure that uncertainties are within the specified range. Quality control procedures should be sufficient to demonstrate that this is the case. The following example is provided for illustration, but should be read in conjunction with the principles underlying assessment limits (Chapter 7) and quality control (Chapter 9):

* Mean value of 20 mg/l. An assessment limit of 70 mg/l is agreed with the SEPA to accommodate design leakage and maintain a good quality of water in the stream. Reliability is not an issue in this instance, and the main concern is to ensure any possible rising trend in data is not masked by poor quality control. A tolerable uncertainty of ±100% (20 mg/l) from baseline mean would not be unreasonable in these circumstances regardless of statistical variation. However, having established the baseline variability within lower limits, a lower tolerable uncertainty limit of say, ±35% (7 mg/l) of baseline mean ought to be attainable.

Data should be evaluated against specified tolerable uncertainty on a periodic (e.g. annual) basis. Where variability exceeds the tolerable uncertainty, this may be due to:

* Excessive errors, which should be remedied by improved quality control.
* Increased natural variability, which may need increased sample numbers to define the natural variation and
* A developing trend. The significance of the trend should be assessed as described in Chapter 7. In this situation, evaluation against tolerable uncertainty would not be feasible until data stabilise around a new mean value.

## Specification of monitoring schedules

### Introduction

The Landfill Regulations specify frequencies at which leachate, groundwater and surface water should be monitored. These frequencies are specified below:

**Leachate Volume**

This should be monitored monthly during the operational phase and six monthly in the aftercare phase although during the operational phase the frequency of sampling could be adapted on the basis of the morphology of the landfill waste but only if SEPA considers that the conditions of the permit should allow for it. In both cases if the evaluation of the data indicates longer intervals are equally effective monitoring may be adapted.

**Leachate Composition**

This should be monitored quarterly during the operational phase and every six months during the after-care phase. In both cases if the evaluation of the data indicates longer intervals are equally effective monitoring may be adapted. However, conductivity must always be measured at least once a year.

**Volume and Composition of Surface Water**

This should be measured quarterly during the operational phase and every six months during the after-care phase. In both cases if the evaluation of the data indicates longer intervals are equally effective, they may be adapted. On the basis of the characteristic of the landfill site, SEPA may determine that these measurements are not required.

**Groundwater Level**

This should be measured every six months during the operational phase and after-care phase. However, if there are fluctuating groundwater levels, the frequency must be increased.

**Groundwater Composition**

This should be measured on a site-specific frequency both during the operational phase and after-care phase. This frequency must be based on the possibility for remedial actions between samplings if a trigger level is reached, i.e. the frequency must be determined on the basis of the knowledge and the evaluation of the velocity of the groundwater flow. In addition, when a trigger level is reached, verification is necessary by repeating the sampling. When the level has been confirmed, a contingency plan set out in the permit must be followed.

Specification of monitoring schedules should result in a series of tables within the site monitoring plan summarising frequency of surveys and monitoring measurements to be undertaken. Examples for a biodegradable landfill site are given in Tables 6.8, 6.9 and 6.10. In finalising schedules for any site, there is a balance to be achieved between the number of monitoring points and monitoring frequency. This can only be judged in relation to the minimum requirements of the Landfill Directive, site-specific conditions and the sensitivity of receptors.

The monitoring schedule should therefore be based on the requirements of the Landfill Directive and on the risk assessment. However, it is recommended that the following guidelines be followed.

**Use of historical monitoring data to satisfy initial characterisation requirements**

At operational landfill sites, or at sites where detailed environmental assessments and risk assessments have been undertaken for planning purposes, monitoring data may already be available. It may be possible to use this data to form all or part of the initial characterisation monitoring records. Such data would be acceptable where they have been quality assured and are statistically valid for their intended purpose. Justification for the use of historical data by the site operator or developer should be documented at the time of submission of the preliminary site monitoring or environmental management plan. Where measurements needed for assessment or compliance purposes are absent from the historical record, specific characterisation programmes may need to be implemented for these.

For operational sites with poor monitoring records, it may be necessary to initiate a specific period of intensive characterisation monitoring in order to establish baseline conditions.

At sites where the model monitoring schedules in Waste Management Papers 4 and 26A have been followed, the retrospective introduction of initial characterisation monitoring programmes may not be necessary if a risk-based monitoring review dose not identify a clear need for this. A review of monitoring results including a statistical summary of all data identifying baseline information should be documented within the site monitoring or environmental management plan.

### Initial characterisation monitoring of groundwater and surface water

**Minimum number of samples for initial characterisation**

Baseline data are those which are characteristic of conditions in the absence of any impacts arising from landfill leachate. The baseline can extend for a considerable period after commencement of landfill operations. However, in order to minimise ambiguity in the interpretation of data following the commencement of landfill operations, it is necessary to gather as much baseline information as possible in advance of landfill development. This is the primary purpose of initial characterisation monitoring for groundwater and surface water.

It is not possible to set universally applicable guidelines specifying the minimum number of samples needed to ensure that initial characterisation monitoring data are statistically valid for their intended purpose. Some authors have suggested a minimum of twenty samples are needed, others sixteen, but all with reservations. The number of samples needed depends ultimately on the baseline variability of the measurement and the tolerable uncertainty required.

In order to standardise approaches for landfill monitoring, the following guidance is given:

* For most landfills, initial characterisation monitoring should be undertaken for at least 1 year prior to landfill development, and wherever possible, for a longer period.
* For sites that can be demonstrated to pose low risks to receptors, initial characterisation monitoring should start at least 3 months prior to deposit of wastes and may be completed following commencement of waste input, subject to agreement with SEPA.
* The monitoring frequency used during the initial characterisation monitoring period should be sufficient to characterise seasonal variation. Normally quarterly or more frequent (e.g. monthly) sampling will be required.
* In the absence of information to support alternative strategies, at least 16 sets of data should be obtained per uniform water body. Lesser requirements would only be acceptable where data are demonstrated to be statistically valid for their intended purpose.
* Where water characteristics are uniform in a water body, samples could reasonably be obtained from a combination of several monitoring points. For example,:
  + 4 monitoring points could be monitored quarterly to obtain 16 samples within a 1 year period and
  + 3 monitoring points could be monitored every 2 months to obtain 18 samples within a 1 year period.
* For situations where local variations in water characteristics are present, initial characterisation monitoring will need to be carefully planned for each monitoring point in order to adequately establish baseline conditions[[13]](#footnote-13).

**Table 6.8: Summary of example monitoring scheme for a biodegradable landfill site posing a moderate to high risk to water receptors**

| **Leachate or water body** | **Monitoring** | **Frequency of monitoring Minimum being monitored1**  **Initial charactierisation2** | **Frequency of monitoring Minimum being monitored1**  **Routine (indicators)** | **Frequency of monitoring Minimum being monitored1**  **Routine (ongoing characterisation)** | **Number of monitoring points** |
| --- | --- | --- | --- | --- | --- |
| Landfill Leachate (within the waste body) | Leachate level  Monitoring point base  Volume removed | Monthly  Six-monthly  Monthly | Monthly  -  Monthly | -  Annually  - | 2 per 5 ha cell plus 1 extraction point4 |
| Landfill Leachate | Leachate level  Volume added  Composition | Site specific  Monthly  Six-monthly3 | Site specific  Monthly  Six-monthly | Site specific  -  Annually | 1 per storage (in surface storage) |
| Landfill Leachate5 (at discharge points) | Volume discharged  Composition | Site specific  Site specific | Site specific  Site specific | Site specific  Site specific | 1 per discharge |
| Landfill run-off6 | Observation  Composition | -  - | Site specific  Site specific | Site specific  Site specific | Site specific |
| Other contaminant sources | Observation  Composition | -  - | Site specific  Site specific | Site specific  Site specific | 1 per within licensed landfill area7 |
| Groundwater | Water level  Monitoring point base  Composition | Monthly  During sampling  See 6.4.3 | Monthly8  -  Quarterly9 | -  Annually  Six-monthly10 | 3 per groundwater system |
| Surface water (in water courses) | Water level  Flow  Composition  Biological assessment | Site specific  Site specific  See 6.4.3  Site specific | Site specific  Site specific  Monthly11  Site specific | Site specific  Site specific  Six-monthly  Site specific | 2 per water course |
| Surface water | Water level  Flow  Composition  Biological assessment | Site specific  Site specific  See 6.4.3  Site specific | Site specific  Site specific  Monthly  Site specific | Site specific  Site specific  Monthly  Site specific | 1 per water (in ponds) |
| Surface water | Composition | As required | As required | As required | 1 per discharge (at discharge points) |

1 Excluding rainfall and other meteorological data, which should be collated annually from site or Met Office data.

2 See Sections 6.4.2 and 6.4.3, which provide specific guidance on initial monitoring frequencies.

3 Increase frequency to quarterly for unstable leachate or polluting sites.

4 i.e. two monitoring points remote from extraction point for leachate level monitoring. Leachate quality monitored in extraction point for cells with complete basal drainage system. For other cells, two leachate sampling points required (e.g. extraction point plus one remote monitoring point.

5 Monitoring programmes will be largely dictated by the conditions of the consent to discharge.

6 Run-off from open landfill surfaces should be separated from contact with waste. Run-off can become contaminated by contact with waste or by accumulation of solids.

7 Examples: wheel washers, fuel storage tanks, chemical stores, waste receipt and handling areas, leachate treatment plants.

8 Decrease to quarterly or six-monthly if normal seasonal fluctuations have been established.

9 Decrease to six monthly or annually if stable conditions are proven or for low risk sites. Increase frequency where groundwater flow velocities are high (see Table 6.10).

10 Decrease to annually if stable conditions are proven or for low risk sites. Increase frequency where groundwater flow velocities are high (see Table 6.10).

11 Decrease to quarterly depending on type of water body and flow rate. Continuous monitoring may be required in sensitive environments.

**Initial characterisation monitoring for biological samples**

Biological measurements are often subject to much greater variability than physical and chemical measurements, and establishment of true baseline conditions may require a period of several years. The initial characterisation period should be used to measure seasonal variation, and to establish any significant correlation between biological and physical / chemical measurements. To achieve this, biological measurements should be:

* Taken at least as frequently as the physical and chemical measurements and
* Co-ordinated with the physical and chemical measurements so that relationships can be investigated.

### Initial leachate characterisation monitoring

Leachate levels and quality can vary significantly over short time periods, particularly during the operational stage of landfilling. It is at the earliest stages of formation that leachate from biodegradable wastes is at its most polluting and hydraulic conditions the least predictable. It is important to characterise the quality of the leachate as soon as possible, especially with respect to List I substances.

To allow for this uncertainty at sites where leachate monitoring is undertaken, an initial period of leachate characterisation monitoring should be carried out in each hydraulically separate landfill cell until:

* Landfilling and final capping, including all barrier and soil layers, have been fully engineered (i.e. capping covers the entire surface area of the cell).
* Hydraulic conditions within the cell are stable and
* Leachate composition has reached a relatively stable state (e.g. methanogenic) demonstrated by a minimum of four sampling events over a period of 2 years.

For many biodegradable landfills, initial characterisation monitoring could reasonably be undertaken monthly for physical measurements such as leachate levels, and six-monthly for chemical composition measurements (Table 6.8). More frequent sampling of leachates for chemical analyses is probably only necessary in a small number of instances. Examples of these would be as follows:

* Where risks are high. e.g. where there is a risk that leachate could escape rapidly from the site in an uncontrollable manner.
* Where leachate is chemically unstable and
* Where water quality analyses are necessary to meet specific compliance conditions.

### Routine monitoring programmes

**Extending the baseline**

If initial characterisation monitoring is unable to satisfactorily establish statistical trends, or if anomalous data are generated at specific monitoring points, it may be necessary to increase the frequency of routine monitoring programmes for specific monitoring points and / or for specific measurements. Details would need to be agreed between the site operator and SEPA and specified within an updated site control and monitoring plan.

All initial characterisation monitoring measurements should be repeated at least annually within the cycle of routine monitoring programmes to provide a screening check. This process ensures that unforeseen changes in non-indicator measurements are not overlooked, and allows an opportunity to review the use of specific indicators.

**Establishing indicators**

The concept of indicator monitoring applies equally to leachate, groundwater and surface water. It allows the use of a selected number of determinands and measurements based on the characteristics of each water body revealed by initial characterisation monitoring programmes and on the risk-based design process. Indicator monitoring measurements should primarily include those needed for regulatory purposes and those to be used to indicate impact by leachate e.g. those for which control and trigger levels have been set. Indicators should be chosen because they are:

* Required by regulation e.g. control and trigger levels.
* Distinctive of leachate in comparison with groundwater and surface water. i.e. indicators that are found at consistently higher concentration in leachate than in groundwater or surface water (e.g. ammoniacal-nitrogen and chloride for a biodegradable site), or causing impacts which are directly related to leachate.
* Relatively easy to measure within specified tolerable uncertainty (Section 6.3.5).
* Mobile, stable and persistent. i.e. unlikely to be retarded or altered while other contaminants pass on ahead (e.g. chloride).
* Complementary. i.e. determinands that do not unnecessarily duplicate information provided by other indicators and
* Used for quality assurance.

The final selection of indicator measurements and monitoring frequencies for any site should be based on knowledge gained from the risk-based monitoring review and from the interpretation of initial characterisation monitoring results.

### Example monitoring schedule

An example monitoring schedule for a biodegradable landfill site posing a moderate to high risk to receptors is provided in Table 6.9. This table illustrates a suite of physical and chemical measurements, which could conceivably be used for characterisation and indicator monitoring. The frequency of ongoing characterisation monitoring for groundwater, surface water and leachate should be at least annual, but a greater frequency may be specified as a result of risk and a review of initial characterisation monitoring data. The frequency of indicator monitoring would be specified in relation to compliance conditions, risk and travel times (see following sections).

The selection of specific monitoring suites and frequencies should always be based on an understanding of the risks and the characteristics of waste, leachate and the surrounding groundwater and surface water. For sites where risks to receptors are low, monitoring schedules need not be as onerous as at sites where risks are high.

### Justification for increasing the frequency of groundwater monitoring surveys

Predicting the rate of movement of leachate contamination in groundwater systems is a complex process involving an understanding of, not only the physical flow mechanism, but also the natural attenuation processes at work. Where these issues have been addressed in a hydrogeological risk assessment it should be possible within the risk-based monitoring assessment to recommend an appropriate monitoring frequency. The recommended frequency needs to take account of three distinct groundwater flow mechanisms:

* Intergranular flow. Groundwater flow is primarily through evenly distributed and interconnected pore spaces. Intergranular flow is in general slower and more predictable than fissure flow. Natural attenuation processes are also more predictable and effective.
* Fissure flow. In formations in which pores are either absent or too small to transmit water freely, water movement may occur primarily through fissures. Flows are less predictable and potentially more rapid than intergranular flow. Attenuation processes are less predictable, though the volume of flow in such instances may provide high dilution. Some formations (e.g. some sandstones) may transmit water both by intergranular and fissure flow and
* Flow in conduits. Flow is almost entirely channelled through discreet solution channels or discontinuities (e.g. in some limestone formations) or man made conduits (e.g. mineshafts / workings). Chemical and biological attenuation processes are likely to be negligible, though dilution can be high. Flows can be as fast as surface water flow.

**Table 6.9: Example of monitoring suites for a biodegradable landfill site posing a moderate to high risk to water receptors**

| **Measurement** | **Leachate within site**  **C** | **Leachate within site**  **I** | **Leachate discharges**  **C** | **Leachate discharges**  **I** | **Groundwater**  **C** | **Groundwater**  **I** | **Surface water**  **C** | **Surface water**  **I** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water level | • | • |  |  | • | • |  |  |
| Mon. point base | • |  |  |  | • |  |  |  |
| Flow rate |  |  | (•) | (•) |  |  | (•) | (•) |
| Vol. Removed | • | • |  |  |  |  |  |  |
| Vol. Added | • | • |  |  |  |  |  |  |
| Vol. Discharged |  |  | • | • |  |  |  |  |
| Temp | • | • | • | • | • | • | • | • |
| DO |  |  |  |  | (•) | (•) | • | • |
| Eh |  |  |  |  | (•) | (•) |  |  |
| pH | • | • | • | • | • | • | • | • |
| EC | • |  | • | • | • | • | • | • |
| TSS |  |  |  |  |  |  | • | • |
| NH4-N | • |  | • | • | • | • | • | • |
| TON (oxidised -N) | • |  | • |  | • | • | • | • |
| TOC | • |  | • | • | • | • | • | • |
| BOD | • |  | • | • | (•) | (•) | • | • |
| COD | • |  | • | • | (•) | (•) | • | • |
| Ca | • |  | • |  | • |  | • |  |
| Mg | • |  | • |  | • |  | • |  |
| Na | • |  | • |  | • |  | • |  |
| K | • |  | • |  | • |  | • |  |
| Alk | • |  | • |  | • |  | • |  |
| SO4 | • |  | • |  | • |  | • |  |
| Cl | • |  | • | • | • | • | • | • |
| Fe | • |  | • |  | • |  | • |  |
| Mn | • |  | • |  | • |  | • |  |
| Cd | • |  | • |  | • |  | • |  |
| Cr | • |  | • |  | • |  | • |  |
| Cu | • |  | • |  | • |  | • |  |
| Ni | • |  | • |  | • |  | • |  |
| Pb | • |  | • |  | • |  | • |  |
| Zn | • |  | • |  | • |  | • |  |
| Other inorganics | (•) |  | (•) |  | (•) |  | (•) |  |
| Phenols | • |  | • |  | (¤) |  | (¤) |  |
| Volatile Fatty Acids | (•) |  | (•) |  | (•) |  |  |  |
| Mineral Oil | (•) |  | (•) |  | (¤) |  | (¤) |  |
| Dissolved methane |  |  | (¤) |  |  |  |  |  |
| Red List | (¤) |  | (¤) |  |  |  | (¤) |  |
| List I / List II | (¤) |  | (¤) |  | (¤) |  | (¤) |  |
| Biological measurements |  |  |  |  |  |  | • | • |

Notes:

See text for explanatory details. Monitoring suites and frequency of monitoring will vary based on site-specific conditions.

See Tables 6.4 to 6.7 for details of measurements and Table 6.8 For example, monitoring frequencies.

Symbols:

C: characterisation measurements.

I: Indicator measurements.

(•): analysed if required by site-specific conditions or for assessment purposes.

(¤): analysed if required by regulatory conditions (e.g. discharge consent or Groundwater Regulations 1998).

The example frequencies for groundwater monitoring set out above are based on the assumption that flow rates are relatively slow. However, there are situations when, in the event of leachate escape through the liner system, the rate of contaminant movement may be more rapid than can be reliably monitored by quarterly or six-monthly surveys, in which case surveys that are more frequent may be needed.

The flow velocity of groundwater in saturated granular formations can be determined by simple groundwater theory where:

V = K.i / n

Where:

V is groundwater flow velocity [Length / Time]

K is hydraulic conductivity [Length / Time]

i is hydraulic gradient [Length / Time]

n is effective porosity [Dimensionless]

Using the above velocity of flow, the travel time, t, to a receptor located a distance, s, from the site would be:

T = s / v

Where:

T is travel time [Time]

s is distance [Length]

Where a significant granular unsaturated zone exists, or where natural attenuation processes are at work, the actual time taken for contaminants to reach the receptor may be significantly greater than the time calculated using the above equation. Where natural conditions are suitable, contaminants may never reach the receptor, while some attenuation processes are finite and may only temporarily delay the onset of contamination. Good site investigation data and careful analysis are required if these elements are to be incorporated into travel time calculations.

For the purpose of this guidance, the minimum groundwater monitoring frequency should be determined in relation to the physical groundwater travel time between the landfill site and potential receptors. The variability of a monitoring measurement (determined from baseline monitoring) will also influence the monitoring frequency.

Table 6.10 presents guidance that is applicable to intergranular and fissured flow. Where travel time to a receptor exceeds two years, there is no reason to increase monitoring frequencies above those given in Table 6.8. Where travel time is shorter than 2 years, increased monitoring frequencies are justifiable. Also, where variability in measurements is high and close to or exceeding the tolerable uncertainty, increased monitoring frequencies would be appropriate.

**Table 6.10: EXAMPLE Groundwater monitoring: examples of minimum survey frequencies based on travel time**

| **Travel time to receptor**  **(months)** | **Minimum recommended monitoring frequency1** |
| --- | --- |
| >24 | Six-monthly |
| <12 to 24 | Quarterly |
| 6 to 12 | Monthly |
| <6 | RA2 |

1 The **range** of measurements used would depend on the risk to the receptor as defined in the risk-based monitoring assessment (Chapter 4).

2 RA - Risk assessment based. Sites in such environments should incorporate engineering and monitoring measures capable of providing early warning of leachate escape (e.g. leakage detection layers, resistivity arrays). These measures must be capable of surviving for the lifetime of the site. Where these are absent, monitoring should be at least monthly at monitoring points between the site and receptors. Where leachate is known to escape from the site, receptors should be monitored at increased frequencies determined by investigation and risk assessment.

For situations in which groundwater travel times to receptors are less than 6 months it is likely that the main flow paths will be via fissures and the effectiveness of conventional groundwater monitoring infrastructure alone in detecting leakage is questionable. In these instances, if a leakage detection layer is operational below a site, this may provide an additional means of monitoring. Where an effective leakage detection layer is absent, and risks to receptors are significant, a minimum of monthly groundwater monitoring on the down-gradient boundary should be carried out, supplemented by at least monthly monitoring of receptors and a re-evaluation of risk to these.

### Justification for increasing the frequency of surface water monitoring surveys

The example frequencies for surface water monitoring within this chapter are based on the assumption that the prime need of monitoring is for characterisation purposes. This will allow an appreciation of the long-term variation in water quality but would not be suitable for detecting short term impacts.

Where there is potentially greater short-term risk to the quality of surface water from leachate, more frequent biological and chemical monitoring including the installation of continuous monitoring systems may be appropriate. Situations in which this should be considered include:

* Where surface water receives treated (or untreated) leachate from a direct discharge point or where there is a threat of overspill from leachate and
* Where the quality of surface water is sensitive to pollution loading, e.g. low flow situations, water used for potable supply, of high conservation value (e.g. SSSI) or designated as supporting salmonid species.

**Biological monitoring frequencies**

If required by risk assessment, routine biological measurements involving community assessments of organisms present at the sampling points may be carried out on a quarterly basis, or even less frequently if seasonal variation has been well established by characterisation monitoring.

Biological measures designed to indicate trends e.g. the measurement of chlorophyll to indicate eutrophication, should be repeated at least monthly. Other biological measures designed to give early warning of toxicity may vary in frequency depending upon the sensitivity of the receptor and assessment of the risks

### Assessment Monitoring

Assessment monitoring is triggered when it becomes apparent that a potential impact from the landfill is probably occurring. This would typically be indicated by breach of an assessment criterion. For groundwater the primary assessment limit is the control level (see Chapter 7).

The specification of assessment monitoring schedules should be based on a re-evaluation of risk using all available relevant monitoring data. The schedule would include those measurements for which potential impacts have been demonstrated, and others that may assist in distinguishing between landfill impacts and changes due to other causes. Assessment monitoring frequencies would be determined by consideration of travel time, and time required for implementing any remedial action. It may be appropriate to investigate further the use of alternative tracers indicative of leachate contamination, such as Tritium. Tritium, where present in leachate can often be used as a positive indicator of leachate contamination in groundwaters and surface waters (see Robinson, 1995, Robinson and Gronow 1996).

Should assessment monitoring become necessary, the schedule should be agreed in consultation between SEPA and the operator.

# Assessment Criteria and Contingency Actions

## Introduction

The Landfill Regulations requires that the operator carry out a control and monitoring procedure. The operator is to notify SEPA of any significant adverse environmental effects revealed by the control and monitoring procedures as soon as reasonably possible. SEPA shall then determine the nature and timing of the corrective measures that are necessary and shall require the operator to carry them out.

Assessment criteria should be set to help assess if an adverse trend in the monitoring data has developed. This chapter presents the principles underpinning the establishment of assessment criteria and contingency actions, which address incidences of leachate contamination. Guidance is given in this chapter as follows:

* Section 7.2: the principle of compliance and the process of assessment.
* Section 7.3: definition and specification of assessment criteria and
* Section 7.4: issues related to contingency actions including site investigation and assessment monitoring.

## Compliance and assessment

The terms compliance and assessment in relation to monitoring can be defined as follows:

* Compliance. The process of complying with a regulatory standard, e.g. the maximum leachate head. It should be noted that, under the Landfill Directive, the compliance level for groundwater quality is specifically termed a ‘trigger level’ and
* Assessment. The process of evaluating the significance of a departure from baseline conditions by reference to an adverse trend in data or breach of a specified limit. Under the Landfill Directive, the assessment criterion for groundwater quality is specifically termed the ‘control level’.

A well-planned method of assessment, agreed between the operator and SEPA will help to:

* Avoid breaches of compliance conditions and
* Levels for groundwater) are breached.

## Assessment criteria

### Definition and purpose of assessment criteria

Assessment criteria are specifications that are intended to draw the attention of site management and SEPA to the development of adverse trends in monitoring data. They should be primarily treated as an early warning system to enable appropriate investigative or corrective measures to be implemented, particularly where there is the potential for a compliance limit to be breached.

The primary assessment criteria for groundwater quality are control levels, which are required by the Landfill Regulations, and are derived as part of the hydrogeological risk assessment process.

Assessment criteria can be developed for several different purposes, such as to provide:

* A means of determining whether a compliance limit has been breached in order to avoid ambiguity, an agreed method is required to determine when breaches have occurred. Apart from the simple instance in which a single measurement in excess of the limit is used to define a breach, a statistical test is needed.
* A means of detecting an adverse trend before a compliance limit is reached this ensures that an early warning system is in place to allow reassessment of risk and implementation of contingency actions before the compliance limit is exceeded and
* A method for assessing monitoring data in relation to other advisory limits or conditions.

The determination of adverse trends and the rules governing what is and what is not a breach of a limit can be a subjective process. Clarity on how these issues will be resolved, is an important part of the licensing process. Guidance is provided in the following sections on the establishment and use of assessment criteria to meet this need.

### Aims of assessment criteria

Assessment criteria should aim to:

* Unambiguously identify adverse trends which:
  + - * In leachates are indicative of departures from design conditions set for leachate levels or leachate quality and
      * In groundwater or surface water are indicative of leachate impacts.
* Allow for variation in water quality from baseline conditions, to accommodate design leakage at the maximum acceptable release rate for the site and
* Allow sufficient time to take corrective or remedial action before impacts can cause harm to the environment or human health.

### Components of assessment criteria

In order to fully define an assessment criterion, up to nine individual elements should be specified in the site monitoring plan:

* Criterion objective. The objective should state the specific purpose for which the assessment criterion is being used. This will be related to one or more of the risks listed in the risk inventory.
* Identification of monitoring points to be covered by the criterion. Criteria may be applied to individual monitoring points (e.g. a single monitoring borehole) or to groups of monitoring points (e.g. all monitoring points in a specific landfill cell, an entire groundwater system, or a surface water body).
* The monitoring measurements to be used. A single indicator measurement (e.g. leachate level, chloride concentration) or a group of measurements (e.g. chloride, ammoniacal-nitrogen, TOC) could be utilised.
* The frequency of measurement. Measurement frequency will be specified in the monitoring schedule and should be commensurate with risk and the need to obtain appropriate data with a sufficient level of confidence for assessment purposes.
* The compliance limit for each monitoring measurement e.g. trigger level for groundwater quality, (where statutory conditions apply). A regulatory limit established in the EASR permit or other relevant document. This will only apply to some measurements.
* An assessment limit for each monitoring measurement e.g. a groundwater control level. A limit usually set below a compliance limit, which if exceeded would trigger pre-determined contingency actions. An assessment limit is not required if the compliance limit itself is being assessed, or if the assessment test (see below) is for an adverse trend rather than being governed by a fixed limit.
* An assessment test for each monitoring measurement. A statistical or procedural test confirming breach of an assessment limit or the development of an unacceptable trend;
* A response time. A maximum specified time (measured from the date of a measurement that confirms a breach in the assessment criterion) in which to implement contingency actions and
* Contingency actions. A sequence of pre-planned actions to be implemented within the specified response time.

Examples of assessment criteria for monitoring data from a hypothetical, biodegradable landfill are presented in Tables 7.1 to 7.4 at the end of this chapter. Criteria are site-specific and need to be carefully developed in relation to local conditions.

### Assessment limits and tests

Assessment criteria are strongly based on assessment limits and tests. These concepts are described below:

**Assessment limit**

This is a level at which conditions would deviate from those predicted. For groundwater quality the assessment limit is a groundwater control level. Establishing assessment limits requires the use of the following sources of information:

* The site risk assessment including details of compliance limits, maximum leachate levels and maximum acceptable release rates derived from engineering design standards; and
* Statistical characterisation of baseline data collected during initial characterisation monitoring. Whenever assessment limits are reviewed after commencement of site operations, the baseline statistics should be updated using any routine monitoring data that forms part of the baseline record.

An assessment limit may For example, be fixed by reference to design leakage calculations with an allowance included for variability from baseline values i.e. a groundwater control level. Alternatively, for leachate head For example, the assessment limit may simply be set at a technically justified value less than the compliance limit, as a means of providing an early warning system.

The acceptance of a maximum acceptable release rate of leakage can lead to difficulties in establishing assessment criteria which need to take account of the possible increase in some water quality determinands. In practice, this means that assessment limits will need either to be re-evaluated periodically or be fixed at a concentration which anticipates an increase above baseline concentrations. In the case of groundwater or surface water which has been subject to remediation, assessment limits may need to be revised downwards periodically until an acceptable quality of water is achieved.

**Assessment test**

The assessment test may be a statistical or qualitative test used to confirm a breach of the assessment limit or the development of an adverse trend. The use of statistical tests to define adverse trends in landfill monitoring data is the subject of ongoing development work.

Examples of statistical tests are:

* A simple breach of the test limit on a single occasion (deterministic approach).
* Probabilistic assessment of breach of the test limit for single determinands using methods such as:
  + - * Control chart rules (e.g. a simple breach of the test limit on a specified number of occasions).
      * Cusum charts and
      * Process capability index.
* Probabilistic assessment of breach of the test limit for multiple determinands using methods such as:
  + - * Multivariate control charts and
      * Water quality indices (e.g. principal component analysis, pollution indices).

The reliability of indices and multivariate control charts is difficult to validate and both should be used cautiously. If poorly designed, both methods can mask trends in individual determinands rather than enhancing their detection.

When a breach in an assessment limit is confirmed by the assessment test, SEPA should be formally notified in writing immediately. At the same time, contingency actions as set out in the sites contingency plan should be implemented within specified response times.

### Minimum use of assessment criteria

Assessment criteria should be used selectively and need not be applied to every single monitoring point or measurement. The following specific assessment criteria should be developed for biodegradable landfill sites or sites where risks to receptors are significant:

* To confirm that leachate levels remain below a fixed maximum level above the site base (expressed as m.AOD). Compliance and assessment limits should be set in relation to risk assessment assumptions used in the design of the site for calculating the maximum acceptable release rate.
* To provide sufficient warning to prevent leachate levels from overspilling to ground surface. Where leachate levels in older landfill sites cannot be practically reduced, maximum leachate levels should be established for the site, to ensure surface outbreaks of leachate do not occur.
* To enable timely action to be taken to prevent deterioration in water quality in groundwater.
* Groundwater control levels should be set as an early warning of a beach in a trigger level. The levels at which, and the determinants for which the control levels are set should be based on consideration of a site-specific risk assessment. To enable timely response to prevent deterioration in water quality in surface waters and
* To monitor the impact of discharges from the site to water courses based on an assessment of the risks posed to the water course e.g. by reference to determinands such as ammoniacal-nitrogen, suspended solids or BOD.

### Problems with assessment criteria

Derivation of statistically based assessment criteria may reveal situations where a compliance limit or assessment limit lies within the baseline data range of groundwater and surface water quality. This will cause obvious difficulties in the design and licensing of the landfill. In such cases, one or a combination of the following actions may be taken:

* Improve the reliability of the assessment of baseline behaviour by reducing uncertainty associated with sampling and analysis. This may be achieved by introducing more stringent sampling protocols and using improved analysis techniques. Variability will be better defined by increasing the number of samples taken (by increasing sampling frequencies or using additional monitoring points) and
* Develop a time-varying (decreasing) assessment limit, using the compliance limit as a target to be achieved by a specified time. This is particularly applicable to situations where remediation has been undertaken and would need to be negotiated between the site operator and SEPA.

### Assessment criteria and breaches

The breach of a compliance limit specified in a EASR permit or associated documents would indicate unacceptable performance of the landfill. Any breach of a compliance limit could lead to costly and time-consuming measures. In the absence of any corrective action being implemented by the site operator, enforcement action may be taken by SEPA. Consequently, all compliance limits and associated assessment criteria should be developed carefully and as a result of consultation between the site operator and the SEPA.

Statutory compliance limits are difficult to change once they have been fixed in a site permit condition. Assessment limits or related conditions which are established within the site control and monitoring plan should be perceived more flexibly. Their intention is to aid in sensibly evaluating monitoring data. When risks are re-evaluated or monitoring data reveals unexpected variation or trends, it may be necessary to review and occasionally change assessment criteria. However, any proposed changes to assessment conditions in the site monitoring plan would need to be technically justified and only implemented after consultation and agreement between the site operator and SEPA.

## Contingency actions

### Procedure in response to breaches in assessment limits

The actions to be taken following breaches of assessment criteria should be specified clearly and linked to a response time. The time period for undertaking any actions would vary from completion on the same day (e.g. for a spillage into a surface water course) to several years (e.g. where more subtle variations in groundwater quality are being evaluated).

In all cases where breaches are confirmed as being due to leachate contamination, a revised assessment of risk should be implemented. Where the risk is proven to be small, assessment criteria may be re-evaluated in consultation between the site operator and SEPA and revisions incorporated into the risk-based monitoring assessment and the site control and monitoring plan.

The steps to be taken in responding to a breach of an assessment criterion, or a pollution incident are:

* Advise site management.
* Advise SEPA.
* Confirm by repeat measurements or observation (if time allows).
* In the case of an obvious polluting incident, initiate pre-planned preventative and / or corrective measures immediately.
* Review existing data.
* Establish the source (if there is doubt) and extent of the problem (by assessment monitoring or site investigation).
* Determine whether the risks caused are harmful to human health or the environment and
* Set in place a procedure for implementing corrective measures or, if risks are acceptable, re-evaluate assessment criteria and monitoring programmes and return to routine monitoring.

Where risks are unacceptable, initiate corrective or remediation measures and establish a strategy for monitoring its effectiveness in consultation with SEPA.

### Emergency action

For many groundwaters, it may take several months or years to evaluate the onset of leachate contamination. In these instances, there should be sufficient time to collate and assimilate data and to initiate corrective measures. In the case of leachate escape into surface water, there may be little time to undertake a formal assessment of the problem. Immediate action may be needed and SEPA should be informed and involved as soon as possible. Contingency measures for such emergencies should be specified clearly.

Examples of situations requiring emergency contingency measures include:

* Overspill or excessive discharge of leachate to a surface water course.
* Leakage from a leachate distribution and pumping system.
* Spillage from fuel storage tanks or other potentially polluting facilities on the site and
* Siltation of surface water courses from site run-off.

All contingency measures should be under constant review and be documented within the site control and monitoring plan/site authorisation documents.

### Assessment monitoring

Assessment monitoring may be required as part of the contingency action, particularly where there is uncertainty as to the cause or full extent of the problem. Typical situations in which increased monitoring may be needed are:

* Departures from design conditions within the landfill site. e.g. to monitor rapidly rising leachate levels (induced, For example, by waste compaction) or to record changes in leachate composition which exceed concentrations used in the risk assessment for designing the landfill and
* To evaluate potential impact on sensitive water receptors if routine monitoring of groundwater or surface water reveals leachate contamination which threatens the viability of a sensitive water receptor (e.g. a borehole abstraction) then more intensive monitoring will be needed to evaluate the risk.

Where assessment monitoring indicates a source of contamination other than leachate, assessment criteria may need to be temporarily suspended in consultation with SEPA. In these cases, baseline conditions need to be re-evaluated so that assessment criteria which are capable of distinguishing and responding to leachate impacts can be re-established.

### Corrective action and remediation

If a breach of an assessment criterion is shown to be due to leachate from the landfill, and a risk assessment has shown that the risk is unacceptable, then remedial action will be required.

Whilst some corrective action may be relatively simple to undertake (e.g. removing an obvious source of pollution such as a leaking pipe) others can be very costly and technically complex (e.g. in-situ groundwater remediation). In all cases, the need for remediation should be balanced against the risk posed to groundwater and surface water receptors and the environmental benefits gained by remediation. In complex cases, specialist advice should be taken and remedial actions and their objectives agreed in consultations between the site operator and SEPA.

**Table 7.1: Example assessment criterion for leachate levels**

| **Contingency action5** | **Response time6** |
| --- | --- |
| Advise Agency. | 1 day |
| Check efficiency of leachate removal systems and initiate contingency actions. | 1 month |
| Report to Agency on re-appraisal of risks to groundwater and surface water and options for corrective measures (e.g. pumping to reduce levels). | 3 months |
| If risks are acceptable:   * document revised assessment criterion to Agency   If risks are unacceptable:   * implement corrective measures | 6 months |

Example is for illustrative purposes only. Exact details will be site-specific.

1 Compliance and assessment limits should be set in relation to hydrogeological risk assessment and engineering design specifications.

2 Y is a lower elevation than X. For example, if the compliance limit from a risk assessment is set at 2m above the site base, an assessment limit for early warning purposes could be set at 1m above the site base.

3 Assessment tests should be capable of providing timely responses. The use of statistical or other tests would be applicable where these can be clearly specified.

4 Level control criteria should be established on a site and cell-specific basis (the above example is only directly applicable to engineered sites with efficient dewatering systems). In some instances, separate criteria may be needed for individual monitoring points.

5 If the compliance limit is breached at any time SEPA must be informed immediately.

6 Response time is measured from the date of measurement (or date of final measurement confirming a breach of assessment limits in the case of multiple measurements).

**Criterion Objective**: To detect an unacceptable permanent rise in leachate levels in a landfill cell.

**Measurement**:Leachate level expressed as m.AOD.

**Frequency**: Monthly.

**Monitoring points**: All leachate level monitoring points in cell A.

**Compliance limit**1: X metres AOD in landfill cell A.

**Assessment limit**1: Y metres AOD2

**Assessment test**3: Mean of all leachate heads exceeds y m.AOD in more than 50% of measurements over a 6-month period4

**Table 7.2: Example assessment criterion for leachate quality**

**Criterion Objective**: To detect an unacceptable deterioration in leachate quality beyond that assumed by risk assessment.

**Measurement**:Chloride (Cl) as mg/l. Ammoniacal-nitrogen (amm-N) as mg/l N, List I substances.

**Frequency**: Six-monthly.

**Monitoring points**: All leachate level monitoring points in cell A.

**Compliance limit**: Not applicable.

**Assessment limit**1: Cl concentration should not exceed Y1 mg/l   
Amm-N concentration should not exceed Y2 mg/l.   
List I substance concentration not exceed Y3 mg/l or detected if not considered in the hydrogeological risk assessment.

**Assessment test**2: Mean C1 or Amm-N concentration from all monitoring points exceeds assessment limit on 3 consecutive days.

| **Contingency action3** | **Response time4** |
| --- | --- |
| Advise Agency. | 1 day |
| Check efficiency of leachate removal systems and initiate contingency actions. | 1 month |
| Agency on re-appraisal of risks to groundwater and surface water and options for corrective measures (e.g. pumping to reduce levels). | 3 months |
| If risks are acceptable:   * document revised assessment criterion to Agency   If risks are unacceptable:   * implement corrective measures | 6 months |

Example is for illustrative purposes only. Exact details will be site specific.

1 Assessment limits should be set in relation to risk assessment and engineering design specifications.

2 Assessment tests should be capable of providing timely responses. The use of statistical or other tests would be applicable where these can be clearly specified.

3 This type of evaluation is unlikely to be subject to immediate enforcement action but would require an urgent re-appraisal of risk. Subsequent enforcement action could include increased controls on waste input.

4 Response time is measured from the date of measurement that confirms the breach of assessment limit.

**Table 7.3: Example assessment criterion for groundwater quality**

| **Contingency action3** | **Response time4** |
| --- | --- |
| Advise Agency. | 1 month |
| Increase survey frequency to monthly | 1 month |
| Undertake site investigation work in cases of uncertainty. | 6 months |
| Report to Agency on re-appraisal of risks and options for corrective measures. | 12 months |
| If risks are acceptable:   * re-evaluate assessment criteria   If risks are unacceptable:   * implement corrective measures | 18 months |

Example is for illustrative purposes only. Exact details will be site specific.

1 Assessment limits (control levels) should be set in relation to baseline data, risk assessment, background groundwater quality and engineering design specifications.

2 Assessment tests should be capable of providing timely responses. The use of statistical or other tests would be applicable where these can be clearly specified.

3 This type of evaluation is unlikely to be subject to immediate enforcement action but would require an urgent reappraisal of risk. Subsequent enforcement action could include increased controls on waste input. Enforcement action would be taken where a trigger level has been beached where no effective corrective measures have been implemented.

4 Response time is measured from the date of measurement that confirms the breach of assessment limit. Response times should be set with consideration for travel times to receptors.

**Criterion Objective**: To detect an unacceptable deterioration in groundwater quality.

**Measurement**:Chloride (Cl) as mg/l. Ammoniacal-nitrogen (amm-N) as mg/l N Selected List I substances (e.g those substances detected in the leachate).

**Frequency**: Quarterly.

**Monitoring points**: Single borehole (e.g. BH1).

**Compliance limit**: Groundwater trigger levels.

**Assessment limit**1: Cl concentration should not exceed X1 mg/l   
Amm-N concentration should not exceed X2 mg/l.   
List I substance below lower reporting limits.  
Groundwater Control Levels

**Assessment test**2: Assessment Limit exceeded on 3 consecutive routine surveys.

**Table 7.4: Example assessment criterion for a discharge to surface water**

**Criterion Objective**: To ensure that consent conditions are maintained. (Applicable for a discharge where monitoring of the discharge by the operator has been agreed or is required by SEPA).

**Measurement**:Ammoniacal-nitrogen (amm-N) as mg/l N.

**Frequency**: Monthly.

**Monitoring points**: Discharge points.

**Compliance limit**1: Amm-N concentration should not exceed X mg/l.

**Assessment limit**2: Amm-N concentration should not exceed Y mg/l3

**Assessment test**4: Amm-N concentration exceeds assessment limit on any 3 occasions in a 6 month period.

| **Contingency action5** | **Response time6** |
| --- | --- |
| Advise Agency and initiate repeat sampling and analysis. | 1 day |
| Report to Agency on results of repeat sampling and analysis. | 1 week |
| Increase survey frequency to 2 – weekly | 2 weeks |
| Report to Agency on re-appraisal of risks and options for corrective measures. | 1 month |
| If risks are acceptable:   * re-evaluate assessment criteria   If risks are unacceptable:   * implement corrective measures | 3 months |

Example is for illustrative purposes only. Exact details will be site specific.

1 Compliance limits will normally be equivalent to consented discharge limits.

2 Assessment limits should be set in relation to risk assessment and engineering design specifications.

3 Y is usually a lower concentration than X.

4 Assessment tests should be capable of providing timely responses. The use of statistical or other tests would be applicable where these can be clearly specified.

5 Enforcement action would be taken in accordance with normal practice for controlling consented discharges.

6 Response time is measured from the date of measurement (or date of final measurement confirming a breach of assessment limits in the case of multiple measurements).

# Design of Monitoring Points

## Introduction

This chapter describes some of the technical issues and design criteria to be applied in the location, design, installation and maintenance of monitoring points.

Guidance is presented in this chapter as follows:

* Section 8.2: describes a number of general issues applicable to the design of monitoring infrastructure.
* Section 8.3: describes issues relevant to identification and referencing of monitoring points.
* Section 8.4: describes design specifications for leachate monitoring points.
* Section 8.5: describes design specifications for groundwater monitoring points and
* Section 8.6: describes specifications for selecting or designing surface water monitoring points.

## General design issues

### Design objectives

The design of monitoring infrastructure should only be finalised after completion of the risk-based monitoring assessment and in the light of the overall monitoring objectives for the site and the monitoring schedules to be implemented (Chapters 4, 5 and 6). This may lead to the abandonment or modification of existing monitoring infrastructure inherited from site investigations and the provision of new monitoring points.

Common design objectives are that monitoring points should be constructed to:

* Prevent mixing of separate sources of water (e.g. leachate and groundwater, surface water with groundwater or different levels of groundwater within strata).
* Use materials which will not influence the measurements being taken and
* Accommodate sampling equipment.

Additional design requirements relate to the protection and safety of monitoring points. Monitoring points should be:

* Designed to physically survive the effects of use, abuse, weather (including flooding where appropriate) and ground movement, for a specified design lifetime the design lifetime for the monitoring point may be less than that of the site. If this is the case, a maintenance and replacement schedule should be provided in the site monitoring plan.
* Protected from vandalism and unauthorised entry.
* Protected from damage by plant and machinery.
* Easily found, and marked to allow identification by personnel unfamiliar with the site.
* Protected from ingress of foreign matter (e.g. dust, rainfall, surface water inflow).
* Sealed (where necessary) to prevent excessive emission of leachate, landfill gas and other natural gases or artesian water and
* Safe for the purpose of monitoring.

Further design objectives specific to different types of monitoring point are given in the appropriate sections below.

### Construction quality assurance (CQA) of monitoring infrastructure

All monitoring installations provided for long-term monitoring within the terms of the site licence should be treated as part of the engineering infrastructure of the landfill site. Poor design and construction of monitoring points can influence and may even invalidate monitoring data. This can lead to misinterpretation of results and the implementation of costly and inappropriate actions. Each point should be designed, supervised and certified in accordance with normal engineering practice. For example, records of borehole constructions should be based on standards in BS5930 (Code of practice for Site Investigations 1999). Health and safety during construction of monitoring points should follow guidance by the Association of Geotechnical Specialists (1992), the British Drilling Association (1981) and the Site Investigation Steering Group (1993).

In practice, this requires the following:

* A design standard shall be agreed with the SEPA for each monitoring point type. This should be incorporated into the site monitoring or environmental management plan for the site.
* A competent person shall take responsibility for the design, installation and completion of each monitoring installation.
* A completion record, log or diagram of each monitoring point shall be prepared and certified by a competent person and incorporated into the site monitoring or environmental management plan.
* Each monitoring point shall be formally registered with the SEPA. Acceptance of monitoring points by SEPA will be assessed against pre-agreed design objectives and
* The continued use of existing monitoring points is dependent on their suitability for the purpose, and the availability of construction details (see 8.5.3 below).

**Defective monitoring installations**

The objective of each monitoring point should be stated within the site control and monitoring plan. Where monitoring points are damaged or unable to meet monitoring objectives for any reason they should be replaced:

* The status of each monitoring point should be reviewed at least annually. Where monitoring points fail to meet their objectives and cannot be remediated, a replacement should be provided within a time period agreed with SEPA or as stipulated in the EASR permit or associated documents.
* All replacement or remediated monitoring points should be certified and recommissioned in accordance with guidance set out above and
* Remediation of existing boreholes for monitoring purposes and procedures for sealing abandoned boreholes are set out in Section 8.5.6.

## Identification and accessibility of monitoring points

The following definitions relating to monitoring points are used in this guidance:

**Monitoring point**: an individual point from which unique sets of monitoring measurements can be obtained.

**Permitted monitoring point**: a monitoring point required by EASR permit or included in the site monitoring or environmental management plan.

**Multiple monitoring points**: A number of monitoring points separated vertically within the same construction or at the same location. This includes any number of monitoring points within a single borehole or situations where surface waters are sampled at different vertical intervals (e.g. a water sample accompanied by a bottom sediment sample).

**Clustered monitoring points**: A group of individual or multiple monitoring points located near to each other for the purpose of monitoring different vertical intervals in strata, waste or surface water.

### Definitions and terminology

The following definitions relating to monitoring points are used in this guidance:

**Monitoring point**: an individual point from which unique sets of monitoring measurements can be obtained.

**Permitted monitoring point**: a monitoring point required by EASR permit or included in the site monitoring or environmental management plan.

**Multiple monitoring points**: A number of monitoring points separated vertically within the same construction or at the same location. This includes any number of monitoring points within a single borehole or situations where surface waters are sampled at different vertical intervals (e.g. a water sample accompanied by a bottom sediment sample).

**Clustered monitoring points**: A group of individual or multiple monitoring points located near to each other for the purpose of monitoring different vertical intervals in strata, waste or surface water.

### Numbering of monitoring installations

A consistent and unambiguous numbering system should be adopted for all monitoring points. The format for numbering will reflect the complexity of the monitoring infrastructure. The following guidelines should be followed:

* Every individual monitoring point used to monitor a specific landfill site should have a unique reference number.
* Short alphanumeric references are preferable (e.g. “GW10”, “S5”, L13”) to enable simple tabulated reports to be prepared and for storage on a computerised database or other recording system.
* Re-use of monitoring point numbers to reference replacement monitoring points should be avoided to prevent confusion and ambiguity with historical data records and
* Monitoring points should only be renumbered where this will improve understanding of monitoring infrastructure or remove ambiguities. Where points are renumbered, any similarity to previous numbering systems should be avoided. An index of new and old numbers should be provided within all future monitoring reports submitted SEPA until this index is incorporated within a revised version of the site monitoring, or environmental management plan and lodged with SEPA.

### Co-ordinates of monitoring points

All monitoring points should be capable of being identified unambiguously. For this purpose:

* Each individual monitoring point should be labelled externally and internally with its unique monitoring point reference number.
* Multiple installations should be identified externally and internally with a unique multiple reference number. Each individual monitoring point should be marked with a separate means of identification (e.g. specific labels, colour coding, or an obvious physical distinguishing feature).
* An up-to-date location plan of all monitoring points shall be incorporated into the site control and monitoring plan and annual review report and
* An up-to-date register of all licensed monitoring points should be incorporated within the site monitoring plan and annual review report. The register shall include the following information.

**All monitoring points**

* Monitoring purpose (e.g. leachate, groundwater, surface water, combined gas and groundwater).
* Name of strata or water course monitored.
* Cell number or site area reference (if relevant).
* Monitoring point reference number.
* Multiple reference number (if relevant).
* Cluster reference number (if relevant).
* Type of monitoring point (e.g. stream, piezometer, standpipe, sump).
* Any safety or access difficulties.
* Distinguishing features (e.g. colour) and
* National Grid Reference (eastings and northings).

**Groundwater and leachate monitoring points**

* Description of datum point used to record water levels.
* Elevation of datum point (normally as m.AOD).
* Datum height relative to ground level (m).
* Original depth of constructed installation (m below current ground level or datum level and m.AOD).
* Diameter of internal lining (mm) and
* Depth to top and bottom of screen or slotted interval (m below current ground level or datum level and m.AOD).

**Surface water monitoring points**

* Description of datum point used to record water levels.
* Elevation of datum point (normally as m.AOD).
* Description of location and
* A sketch plan or photograph of the monitoring point (if necessary).

Example forms for compiling monitoring point registers are included in Appendix 1.

## Leachate monitoring points

### Types of leachate monitoring point

Leachate monitoring points can be classified by their location, which can be:

* Within leachate drainage systems.
* Within leakage detection layers below basal lining systems.
* At storage lagoons, storage tanks and discharge points and
* Within the body of waste.

At any one site, monitoring points may be provided in one or a combination of locations. The largest category at existing landfill sites consists of monitoring points within the body of the waste.

### Design objectives for leachate monitoring points

**Monitoring points within leachate drainage layers**

Specific design objectives relating to monitoring points within leachate drainage layers are:

* To enable an appropriate sample of leachate to be obtained from the base of the site where drainage systems are working efficiently, particularly where recirculation of leachate has been successfully established, samples taken from a discharge point within the basal drainage system will be representative of free-draining leachate within the waste mass and
* To determine the volume of leachate discharged discharge points from drainage systems can be monitored to record the volume removed and, in some instances, the rate of flow of leachate.

Other design objectives are based on an appreciation of the specific purpose of a monitoring point combined with an understanding of the hydraulic conditions of the landfill and the drainage layer.

Monitoring points installed within drainage systems which are part of a continuous drainage blanket could be used to provide leachate level measurements above the site base. Noncontinuous drainage layers are unlikely to be as reliable unless there is free movement of leachate through the waste between drainage lines.

**Monitoring points within leakage detection layers**

The primary design objective relating to monitoring points within leachate leakage detection layers below landfill liners is:

* To identify and quantify any leachate leakage and
* To enable an appropriate sample of liquid to be obtained for comparison to leachate quality.

Depending on the design of the detection layer, other monitoring objectives may be set which could include the measurement of water level, flow or discharge rate.

Leakage detection layers provide, in theory, a monitoring facility for detecting any leakage of leachate below the base of an engineered basal lining system. The design of detection layers usually includes a granular material, sometimes with piped drains, sandwiched between low permeability layers. The detection layer should remain dry in the absence of any leachate leakage from the overlying landfill. In practice, water can enter this layer from various sources including the following:

* From compaction of an overlying mineral lining layer releasing pore water following construction. The quality of this water can often be heavily mineralised and be mistakenly identified as leachate and
* From groundwater upwelling through the secondary basal liner. This can occur seasonally or permanently depending on local conditions. However, it should be bourn in mind when designing a landfill that the Landfill Regulations require that groundwater should be prevented from entering the landfilled waste and that designing the base of the landfill below the water table can pose engineering problems.

In both cases, a sample of the pore water from the basal lining materials used should be obtained to allow comparison to any water identified in the detection layer.

Where leakage detection layers are in place and successfully operating, they could provide a rationale for reducing monitoring effort in groundwater and surface waters provided:

* The detection layer can be hydraulically tested to confirm its integrity.
* At least 5 years monitoring data is available from the detection layer and from surrounding groundwater and surface water and
* Monitoring data from the detection layer shows no evidence of leachate leakage.

If leakage of leachate into the detection layer is confirmed, an immediate review of risk and the need to modify groundwater and surface water monitoring programmes should be implemented.

**Leachate lagoons, storage tanks and discharge points**

Specific design objectives relating to monitoring points within surface storage lagoons and at discharge points include:

* To permit an accurate level of fluid within storage facilities to be measured and recorded to an elevation expressed as metres above ordnance datum or by reference to a locally fixed maximum or overspill level.
* To enable a sample of leachate representative of the lagoon quality to be obtained prior to discharge and
* To record discharge volumes.

Lagoons may include storage facilities pre and post treatment or collection facilities prior to discharge off-site via tanker or sewer.

**Monitoring points within the body of waste**

Specific design objectives relating to monitoring points within the body of the waste are:

* To permit an accurate level of leachate to be measured and recorded to an elevation expressed as metres above ordnance datum and as metres above the site base and
* To enable an appropriate sample of leachate to be obtained from the waste body.

Other design objectives are based on an appreciation of the specific purpose of a monitoring point combined with an understanding of the hydraulic conditions of the landfill. Some examples follow:

* Monitoring points may be designed for multiple use such as gas monitoring, gas extraction, and / or leachate extraction. Multiple usage of monitoring points should only be accepted where it can be shown that these do not conflict with basic monitoring objectives. For example, a leachate extraction point which is frequently pumped will provide a reasonable point for obtaining leachate quality samples but may not always be satisfactory for level monitoring (Section 6.2).
* Leachate quality may vary with depth. The sampling zone specified in the design objective will depend on whether the monitoring objective is to sample leachate from the base of the site (e.g. for risk assessment of leakage through base) or leachate from higher levels within the waste (e.g. to assess variability in degradation of the waste body) and
* Perched leachate levels may be developed in the site, and these may require separate additional monitoring installations.

In some circumstances, it may not be possible to fully achieve design objectives. Some examples follow:

* Larger diameter sumps may not yield samples of leachate appropriate to the waste body unless they are regularly pumped. It is preferable to use smaller diameter installations (i.e. less than 200 mm) for routine monitoring and
* In high density or deep landfill sites without a leachate collection and basal drainage system, it may prove difficult to provide monitoring points that can unambiguously record the level of leachate lying above the site base. Levels in these monitoring points may be influenced by perched inflows or confining pressures induced by the weight of overlying waste. In cases of ambiguity the lack of certainty should be compensated by greater emphasis on the potential pollution pathway - i.e. by increasing the number of points and the frequency of monitoring of groundwater or surface water.

In cases where it is not technically possible to obtain unambiguous leachate monitoring information from a site, these reasons should be stated in the site control and monitoring plan and an alternative monitoring strategy developed in consultation between the operator and SEPA.

### Design and construction of leachate monitoring points in the body of waste

There are many individual and innovative approaches used in the design and construction of leachate monitoring points within waste. In general, these fall into two categories:

* Monitoring points built during landfilling and
* Monitoring points retrofitted following landfilling.

Advantages and disadvantages of each category of monitoring point are summarised in Table 8.1. The optimum approach would be to use a combination of both types. Guidance on the design and construction of these points is presented in Appendices 3, 4 and 5.

**Table 8.1: Advantages and disadvantages of built and retrofitted monitoring points for monitoring leachate**

| **Type of Leachate Monitoring Point** | **Advantages** | **Disadvantages** |
| --- | --- | --- |
| Built | 1. Installed on site base. 2. Ability to monitor, 3. Extract from basal drainage layers. 4. Ability to obtain monitoring data during landfill operations. | 1. Substantial foundations needed. 2. Above basal engineering layers to prevent puncturing and to maintain verticality; susceptible to damage or lateral movement during landfill operations and construction. 3. Concrete rings liable to chemical disintegration 4. Can impede capping and restoration. |
| Retrofitted | 1. Can be drilled vertically. 2. Annular design and seals. 3. Can be better controlled. 4. Greater density of boreholes. 5. Can be constructed where needed. | 1. Difficult to complete on site base where there is a risk of puncture to basal seals. 2. Drilling is potentially hazardous. 3. Unpredictable drilling problems can occur. 4. Installations greater than 30m deep often need large specialist drilling rigs. |

When sampling from monitoring points in the waste body there may be a need to dispose of purge water (see Section 9.9). In some cases, an appropriate option for disposal is by use of a specially constructed purge water disposal point to enable return of purge water into the waste body directly below the restoration layers. This would need to be installed either at the time of restoration (for monitoring points built during landfilling) or when the monitoring point is constructed (for retrofitted monitoring points).

### Construction quality assurance (CQA) and borehole logs

CQA procedures should be adopted to certify and document each structure prior to formal commissioning of its use and acceptance by SEPA. Detailed construction drawings or borehole logs for each monitoring point should be provided within the site control and monitoring plan.

A further CQA document should be issued when structures are completed to final level. Construction logs and survey details for all monitoring points should be incorporated into the site control and monitoring plan.

### Maintenance and ongoing quality assurance of infrastructure

The depth to the base of all leachate monitoring points should be recorded at least annually, to check for evidence of silting or blockage. Problems with access of monitoring equipment should also be recorded. This information should be used at the time of the periodic review (see Chapter 10) to assess whether monitoring objectives are being achieved. A monitoring point which is gradually silting-up and is of sufficient diameter, may be cleaned by use of a bailer operated with a cable percussion rig, although there is a risk of damage to linings, particularly if they are pinched or no longer vertical. Smaller diameter boreholes may be cleaned using a surge block and pump. Use of compressed air or vacuum for cleaning is also possible but requires a system for full control of the leachate discharge to avoid health and safety risks.

A leachate monitoring point that is silting-up rapidly or has a broken or deformed liner, should either be:

* Adapted for monitoring a shallower depth range if this is feasible and meets a monitoring objective or
* Decommissioned and replaced.

Procedure for the decommissioning of redundant monitoring points in waste should be reviewed with SEPA.

### Novel or remote monitoring points

Any monitoring point design which involves indirect monitoring methods (e.g. the use of buried transducers for level monitoring or electrodes for resistivity measurements) or any design involving monitoring through non-vertical structures (e.g. sampling through inclined side wall risers) should be used only where such structures can meet the basic monitoring objectives set out above. Any novel monitoring point designs should be either based on proven technology or proven in parallel trials with methods that are more conventional until their long-term integrity can be guaranteed.

**Resistivity arrays**

Resistivity arrays constructed in the unsaturated zone below landfill sites to detect leachate leakage should be designed to be:

* Constructed below the whole or specific parts of the landfill where leachate is most likely to be concentrated.
* Protected from damage and proven through regular operation and calibration checks to be operational and reliable.
* Capable of detecting resistivity variations due to leachate impact against natural resistivity variations established from a period of seasonal baseline monitoring and
* Supported by alternative physical monitoring systems (e.g. a leachate detection layer and / or groundwater monitoring boreholes). Over-reliance on remote monitoring systems should be avoided.

## Groundwater monitoring points

### Types of groundwater monitoring point

Terminology applied throughout this guidance to different types of groundwater monitoring point is as follows:

**Well; borehole**: “a hole sunk into the ground for abstraction of water or for observation purposes. A well is generally of larger diameter than a borehole and dug rather than drilled. A borehole is often used for monitoring purposes only and may be lined with suitable casing and screened at appropriate depths” (ISO 5667, Part 11, 1993).

**Open or longscreened**

**borehole**: An open borehole or a lined borehole of any diameter which is screened throughout the majority of its length. For the purpose of this guidance a “long screen” is defined as greater than 6m in length.

This is sometimes referred to as a “traditional observation borehole”

**Piezometer**: A tube installed to allow water level measurement and sampling from a specific vertical interval (the ‘response zone’). The response zone consists of a porous or short screened section (i.e. typically less than 6 m in length), or pressure measuring device, isolated by annular seals.

**Nested piezometers**: A borehole containing more than one piezometer separated vertically by seals.

The installation of more than two piezometers in a single borehole for monitoring purposes should not be undertaken other than in exceptional circumstances and in consultation between the operator and SEPA. It is inadvisable to install more than one installation in a borehole without experienced and careful supervision due to the difficulties in obtaining an effective seal. Even if installed correctly, nested installations can give monitoring results that are ambiguous.

**Clustered piezometers**: A group of piezometers drilled close together, to monitor separate vertical intervals in the underlying groundwater or waste formations.

These are sometimes referred to as “multiple observation boreholes”

**Multi-level sampling**

**Devices**: Multi-level sampling devices These are proprietary systems, which provide a means of sampling from a number of small diameter ports or short-screened sections separated by vertical seals. Seals are either installed manually (in the manner of nested piezometers) or by the use of packers or other inflating mechanism.

The installation of specialist multi-level systems should be undertaken in consultation between the operator and SEPA. A detailed installation specification, supervision and performance testing would be required wherever these types of installations are used.

### Design objectives

Specific design objectives relating to groundwater monitoring points are:

* To permit an accurate water level or pressure (“piezometric”) level of groundwater to be measured and recorded to an elevation expressed as metres above ordnance datum and
* To enable an appropriate sample to be obtained from the surrounding stratum.

Other design objectives are based on an appreciation of the specific purpose of a monitoring point combined with an understanding of local hydraulic conditions. Some examples follow:

* Monitoring points may be designed for combined use as gas monitoring points. Multiple usage of monitoring points is to be encouraged where these do not conflict with basic monitoring objectives. However, the basic design of most gas monitoring points has historically been based on the provision of boreholes with a continuous long-screen. These types of design will introduce vertical pathways in layered strata which invalidate their use for reliable groundwater monitoring and should be avoided (see IWM Landfill Gas Monitoring Working Group 1998).
* In strata in which groundwater level varies seasonally, the screened section of the borehole should extend below the lowest likely water level by sufficient depth to enable sampling and
* In strata in which vertical flow of water or dispersion is dominant (upwards or downwards) clustered or nested piezometers or longer screened installations may be necessary to effectively monitor contaminant flow.

In layered strata in which water flow is directed horizontally between low permeability layers, clustered (or possibly nested) piezometers could be required to effectively monitor contaminant flow. In some situations a composite sample may be acceptable (usually across relatively thin layers), in which case a continuous screened section would be appropriate.

### Design and construction of groundwater monitoring points

Groundwater monitoring points may be established by:

* using existing groundwater discharges and abstractions.
* using existing monitoring points and
* constructing new installations.

Existing structures should only be used if they are capable of fulfilling the monitoring objectives for the landfill site. Borehole logs and well design details are essential to evaluate the usefulness of any point in relation to groundwater flow which may be potentially contaminated from landfill leachate.

Guidance on the construction of new monitoring borehole installations is provided in Appendices 4 and 5.

**Use of existing groundwater discharges and abstractions**

These include springs, water supply boreholes or wells. In many cases, a groundwater discharge or abstraction will be identified as a receptor in the risk-based monitoring assessment. Monitoring receptors directly would not provide sufficient early warning of potential problems and consequently discharges or abstractions would normally only be monitored if:

* There is uncertainty associated with the pathway monitoring.
* The discharge is itself on a pathway to another downstream receptor and
* Monitoring of the discharge will significantly enhance understanding of the hydrogeology of the site.

Large-scale water supply or other abstractions draw water from a large area and are likely to greatly dilute any impacts from landfill contamination except in case of gross pollution. Their use as monitoring points is questionable. If abstractions are operating or flowing at relatively low rates, the dilution potential will be less and these points may be suitable for monitoring purposes. Abstraction records should be maintained as part of the routine monitoring of such points.

**Use of existing monitoring points**

These may include monitoring points installed for other monitoring purposes by adjacent landowners or SEPA, or for site investigation. Older monitoring points often consist of open or long-screened boreholes, which may be unsuitable for site monitoring purposes. They may even present a contamination hazard in themselves by providing a direct connection between water-bearing strata. Other monitoring points may consist of piezometer installations, which are more suitable for direct incorporation into a landfill monitoring programme. In either case, an evaluation against monitoring objectives should be carried out, and one of the following options implemented:

* Allow the monitoring point to be used for its existing purpose, but do not incorporate it into the landfill monitoring programme.
* Incorporate the borehole without modification into the monitoring programme.
* Modify the borehole construction for incorporation into the monitoring programme and
* Abandon the borehole by grouting and capping.

A monitoring point may only be included in the programme if its construction and geological details have been determined from records or geophysical logging. If a long-screened or open borehole is to be modified, this may be done by either:

* Backfilling so that it is open only to a few metres of the uppermost aquifer. No vertical pathway to the lower section of the hole should remain, so this option may not be feasible for lined boreholes, unless the liner can be withdrawn and any gravel pack effectively sealed OR
* Installation of nested piezometers to permit monitoring at separate vertical intervals. This modification is only possible in larger diameter boreholes (e.g. >200 mm) in which lining has not been installed and should otherwise be discouraged.

The data already available from an observation borehole should be taken into account when the future of a borehole is decided. A quality or water level trend covering many years has an obvious value as a baseline against which changes can be measured. There are three choices:

1. Not to implement any changes and continue to collect data.
2. Modify the borehole to an improved design. Mark the date of change in all databases so that any changes in behaviour can be related to the change in design and
3. Drill a new monitoring point to an improved design adjacent to the existing point. Monitor both points for one year to obtain data for correlation between the old and new trends, then abandon and seal the old borehole.

**New groundwater monitoring boreholes**

Construction of new boreholes allows monitoring points to be located and designed specifically to meet the monitoring objectives. The method of drilling, lining materials, screen design and sealing method should all be given careful consideration to ensure that the monitoring objectives are met.

Guidance related to drilling and completion of groundwater monitoring points is included in Appendices 4, 5 and 6.

### Groundwater borehole cleaning and development

Following installation, each monitoring borehole should be cleaned out and developed to remove silt and other fine materials from the lining, gravel pack and surrounding strata. Cleaning and development in most monitoring boreholes can be undertaken either on completion of the installation or as part of an extended preliminary sampling survey by simply pumping and surging the borehole for a period of time. It may take the removal of ten or more borehole volumes of water to achieve reasonable cleaning and development of a borehole. Where geotextile wraps are used, lesser volumes of water may need to be removed depending on the strata sampled. Where strata are predominantly silty or clayey in nature, it may not be possible to achieve a sediment free discharge. Further guidance is included in Appendices 5 and 6.

### Construction quality assurance (CQA) and borehole logs

CQA documentation and borehole logs should be produced and collated into the site monitoring or environmental management plan as specified for leachate monitoring points (Section 8.4.4).

### Groundwater borehole maintenance

Most groundwater monitoring boreholes will require periodic maintenance. The most common problem is associated with silt accumulation in the base of a borehole, which can completely block screened intervals. Boreholes may also become blocked due to pinching of the lining or by foreign objects. Depths can be checked by comparison with details in borehole logs. If borehole logs do not exist, it may be necessary to carry out a caliper, geophysical or camera survey to help identify construction details (Appendix 7).

Boreholes which are silted can be unblocked by surging (e.g. by the addition of water combined with a pump such as an inertial pump) or by the use of “air-lift” methods (i.e. using a pressure jet to blow out the silt, though uncontrolled air-lift methods are not suitable for contaminated groundwater which may present a health and safety hazard). Further details are provided in Appendix 6.

Any boreholes that cannot be rehabilitated should be replaced as soon as possible. The damaged borehole should be sealed and capped in order to remove a potential pathway for contamination of groundwater. Procedure for the abandonment or decommissioning of redundant boreholes should be reviewed SEPA. In general, abandoned boreholes should be sealed with cement-based grout or bentonite and capped in a manner that prevents any confusion with active monitoring points. The site control and monitoring plan, drawings and monitoring point register should be amended to clearly document the abandonment.

## Surface water monitoring points

### Selection of surface water monitoring points

Factors to be considered in the selection of surface water monitoring points are:

* The appropriateness of the sampling point to meet monitoring objectives.
* The measurements to be made (physical, chemical or biological sampling).
* The sampling method and
* Accessibility and safety.

Sampling locations should be chosen to allow access with minimal disturbance of the water at the time of sampling.

**Monitoring points in water courses**

Monitoring points should be located up and downstream of discharges from a landfill site. The downstream monitoring point should be located close enough to the discharge to assess any changes related to the discharge, but far enough downstream to ensure adequate mixing. More than one monitoring point should be chosen downstream of the discharge if information on the extent of impact or recovery is required. The choice of more than one reference point upstream of the discharge would increase confidence in the description of reference conditions.

**Monitoring points in ponds, lakes and wetlands**

Monitoring points should be situated in an area that is sufficiently representative of the water body as a whole. Various factors introduce heterogeneity into water bodies, e.g. inflowing and outflowing water and currents, depth variations, and in deeper waters, stratification of the water. In large bodies of water, more than one monitoring point may be required to reflect lateral and vertical variations in water chemistry.

**Monitoring at discharge points**

Discharges may be pumped intermittently, be free-flowing through piped outlets or be pond overflows. The monitoring point needs to be chosen in order to obtain a sample which is sufficiently representative of the quality of the discharge before it is mixed into the receiving water course.

**Sediment samples**

Sediment samples taken from bottom sediment deposits can sometimes provide a very sensitive means of identifying impacts on surface water by contaminants such as trace metals, which are readily adsorbed onto sediment from flowing water. Care and expertise is required in selecting sampling locations, so that:

* Sites which are depositional in nature are chosen, taking account of seasonal patterns of accretion and erosion.
* Sampling depth is chosen to reflect recently deposited sediment and
* Upstream and downstream sampling sites are chosen which are comparable.

Consideration should also be given to the relationship between contaminants in solution, in the suspended sediment and in deposited sediment, in order to derive an appropriate sampling regime.

**Biological samples**

Biota sampling requires an understanding of habitats, sampling method and measurement technique. Further guidance is provided in Standing Committee of Analysts, 1996.

### Objectives for the selection or design of surface water monitoring points

Specific objectives that are applicable to selecting or designing surface water monitoring points are:

* To permit an accurate water level to be measured and recorded to an elevation expressed as metres above ordnance datum.
* To permit an estimate of flow to be measured and
* To enable an appropriate sample for surface water quality measurements.

Other design objectives are based on an appreciation of the specific purpose of a monitoring point combined with an understanding of local hydraulic conditions. For example,:

* To enable an appropriate sample for biological quality of surface water to be obtained and
* To enable an appropriate sediment sample to be obtained.

# Monitoring Methodology

## Introduction

To ensure data collected by all monitoring personnel are appropriate and collected in a consistent manner, the methodology used for monitoring should be standardised and subject to quality control checks. By using standardised procedures and competent personnel, greater consistency in data collection can be achieved. Poor quality or ambiguous data can lead to serious difficulties in interpretation.

Monitoring methodologies should be adopted for each site based on current good practice and in accordance with the specific monitoring objectives for the site.

Guidance in this chapter is presented under the following headings:

* Section 9.2: Objectives of methodology.
* Section 9.3: Safety of monitoring personnel.
* Section 9.4: Specification and quality control of methodology.
* Section 9.5: Physical monitoring measurements.
* Section 9.5 to 9.12: Collection and analysis of water quality samples.
* Section 9.13: Collection of quality control samples and
* Section 9.14: Documentation of procedures and results.

## Objectives of monitoring methodology

The principal objective of all monitoring methods is to ensure that the measurement is sufficiently reliable for the purpose intended, i.e. that an appropriate sample or measurement is taken. For example,:

* If the monitoring objective is to determine the groundwater quality in strata down-gradient of the landfill site, then the analysis results should be sufficiently representative of groundwater in the strata, and should not be excessively influenced by the borehole design, sampling methodology, cross contamination from other sources, or analytical method.

Similar examples could be cited for leachate or surface water samples.

Reliability is achieved by controlling errors introduced by the monitoring process. In order to reduce errors to appropriate and known levels, quality control procedures need to be used.

The following quality objectives should be applied to any monitoring methodology:

* Each sample or measurement at a specific monitoring point should follow a consistent and reproducible procedure. This is achieved by using approved and documented monitoring protocols. Records should be kept of conditions at the time of sampling and of any deviations from specified protocols.
* The sample collected or measurement made should not be excessively affected by contamination from surface run off, contact with the sampling equipment, or extraneous matter that may have entered the monitoring structure. Nor should it be affected by the products of reaction with materials used in the construction of the monitoring point. In order to avoid unnecessary cross-contamination of monitoring points, any equipment which is used to directly sample or temporarily store leachate or any other contaminated water, should never be used for groundwater or surface water monitoring. Wherever practical, dedicated or disposable monitoring equipment should be used for sampling, particularly for leachates or other contaminated waters. Where this is not practical, decontamination protocols should be used in conjunction with equipment blank samples to determine the effectiveness of the decontamination effort. Where monitoring points are known or suspected to be contaminated, sampling should proceed from least to most contaminated waters.
* A sample that is to be analysed should not be significantly different from its chemical and physical state at the time it was sampled. Analytes which are susceptible to contamination or reactions within sample containers should either be measured on site or fixed using a preservative.
* Analytical methods should not be excessively affected by cross contamination, poor recovery, interference or instrument errors. Analytical methods should be chosen which are appropriate for the medium and the sampling objective.
* It should be possible to authenticate all measurements. Proper documentation should be produced in the form of field records and chain of custody documentation and
* Where measurements are critical for assessment or compliance purposes, the errors associated with monitoring should be quantified. This is achieved using quality control sampling methods.

A specific objective of all monitoring programmes is to ensure that work is undertaken in a safe manner. This specific issue is dealt with in the following section. The remaining sections of this chapter provide guidance on methodology appropriate to different types of monitoring measurement.

## Safety of monitoring personnel

All monitoring points should be selected or designed with the objective of providing clear, safe and unobstructed access for monitoring personnel using designated monitoring equipment.

Monitoring personnel should never be required to undertake monitoring in unsafe conditions. Monitoring points that pose particular difficulties for access or are unsafe in any way should be identified within the site control and monitoring plan. Any protective health and safety measures needed to access these points should be documented. These points should only be accessed following receipt of instructions and the provision of any necessary training or support by personnel familiar with the hazards.

Specific instances where health and safety briefings and/or training should be provided, or where more than one person should be deployed are:

* Where it is necessary to manually lift equipment or remove obstructions which are greater than 25kg in weight or are shaped awkwardly for one person to handle safely.
* Where access to a monitoring point cannot be achieved easily from a position standing at normal ground level.
* Where monitoring points require access within a confined space.
* Where leachate sumps or monitoring points are venting landfill gas under pressure and no protective headworks are fitted.
* Where leachate monitoring points are located within active landfill areas.
* Where stream samples are to be taken from unsafe bank positions.
* Where monitoring requires the use of a boat and
* Where monitoring involves the handling of chemical reagents which may be hazardous to health.

The above examples are not exhaustive and a proper health and safety risk assessment of each monitoring point should be implemented. Guidance on sampling safety is provided in ISO 5667 Part 1 (general issues), Parts 4 and 6 (surface water) and Part 11 (groundwater). Where chemical reagents are handled during sampling, samplers should be familiar with COSHH Assessments[[14]](#footnote-14) and hazard data for these substances.

## Specification of monitoring protocols

### Specification of measurements

Measurement specifications need to be based on an overall understanding of the tolerable uncertainty specified for the measurement (Section 6.3.5), the measurement method, and the practicality of implementing and controlling measurements under field and laboratory conditions. Finalising specifications will normally be an iterative and consultative process involving field personnel, the analytical laboratory and site management. It may take several sampling surveys to achieve a workable standard that can be routinely applied to a particular set of monitoring points.

The tolerable uncertainty specified for any measurement (Section 6.3.5) will influence the selection of methods and quality control procedures used for the measurement. For example, there is little point in specifying analytical accuracy to parts per billion if the design of the monitoring point is not understood, sampling technique is poor or laboratory methods are incapable of achieving this standard.

A measurement specification should include:

* The measurement method.
* A detailed protocol for sampling / measurement and record keeping and
* An appropriate level of quality control sampling and measurement.

### Monitoring protocols

In order to present clear instructions to field personnel and analytical laboratories, standardised protocols for monitoring procedures should be specified in the site control and monitoring plan. The elements involved in devising monitoring protocols emphasise the importance of ensuring that procedures are formalised not only with field personnel, but also with the laboratory responsible for analyses of samples. Example field forms are included within Appendix 8 and a generalised sampling protocol as Appendix 9.

Given the length of time over which some monitoring programmes extend, changes in monitoring protocols are inevitable. Examples include a change in purging method or a change in analytical laboratory, or even a change in sampling and analytical personnel. Changes in protocols should be managed carefully to ensure that the new protocol meets monitoring objectives and tolerable uncertainty values specified in the site control and monitoring plan. It may be appropriate, particularly for measurements used for compliance purposes, to take a series of duplicate and other QC sample measurements using the old and new protocols to record the magnitude of change. Without this information, historical data records can sometimes become difficult to interpret and in some instances could result in the validity of an entire baseline record being brought into question.

## Physical monitoring measurements

### Preamble

Physical monitoring measurements include observational, water balance, flow and level measurements (see Table 6.4).

### Observational records

Observational records include:

* Observation of surface water run-off from landfill areas.
* Observation of other contaminant sources.
* Observation of vermin and
* Observation of vegetation.

These observations are part of the normal daily management routine of most operational landfill sites, and significant observations should be logged formally as part of routine monitoring procedure.

An example form for maintaining observational records is included in Appendix 8. Where appropriate these should be accompanied by a photographic record.

### Water balance measurements

The following sections provide guidance on the measurements that can be taken routinely, to allow interpretation of water balance at a landfill site.

This group of measurements (listed in Table 6.4) includes:

* Rainfall and other meteorological data.
* Volume removed.
* Volume added and
* Volume discharged.

The last three measurements can be grouped together as “leachate management records”.

**Rainfall and other meteorological data**

Rainfall records for the majority of sites can be obtained from the Met Office. Site records can be used where these are available, though they should be periodically compared to Met Office records to check consistency. The level of detail will vary from site to site. For example, a statement of mean annual rainfall and effective rainfall for a number of different types of surfaces may be sufficient. At sites where risks are significant, monthly summaries would normally be needed.

**Leachate management records**

Records should relate to cell by cell distribution of water within site based on recirculation, pumping or discharge records. Most of these can be collected as part of the normal daily operation of a landfill site.

Records, however simplified, should be maintained (e.g. by counting bowsers or estimating pumping volumes from fixed pumps by recording running hours). Where flow meters are used these should be calibrated and read as frequently as possible (at least monthly).

Information is best summarised monthly and reviewed annually in comparison with rainfall and water level measurements. Source records should be maintained for checking.

Example summary forms for recording monthly water movement within the site are included in Appendix 8.

### Level and flow measurements

Routine groundwater or leachate level measurements from monitoring points should record the rest water level. If pumping is being carried out from either the monitoring point to be measured or an adjacent monitoring point, this could produce misleading level measurements. When water is pumped from a monitoring point, the water in the lining will fall to a level at which the rate of inflow (i.e. the yield) matches the rate of pumping. This level is the “pumping water level”. Dewatering will temporarily occur if the inflow rate for the entire depth of the monitoring point is less than the pumping rate. When pumping is stopped, groundwater (or leachate) will continue to flow into the monitoring point until it reaches the rest water level sustained in the surrounding strata or waste.

The time taken for levels to recover after pumping can vary from being almost instantaneous to hours, days or longer, depending on the permeability of the surrounding strata or waste and the design of the monitoring point. Where pumping is routinely carried out from monitoring points, the following procedure should be followed:

* A recovery test should be undertaken before confirming the suitability of the monitoring point for routine water level measurements. The test should record water levels from the time the pump is switched off for a sufficient period until the rest water level is proven. This data should be plotted onto a graph of water level against time. A “recovery time” should then be designated to the monitoring point and used to govern the timing of all future water level measurements.
* All water level measurements taken at pumped monitoring points should be accompanied by a record of the interval between the time the pump was switched off and the time of measurement. This time should be no less than the designated recovery time for the monitoring point.
* Tests should be repeated annually to ensure the efficiency of the monitoring point is sustained.
* Unless the time of recovery is known and properly documented in the site monitoring plan, it is unacceptable to use pumped installations for water level measurements and
* Pumped monitoring points in which the recovery time is greater than 24 hours should not normally be used for routine water level measurements.

Pumping from one monitoring point may temporarily lower water levels in adjacent non-pumping monitoring points and give a false impression of the real rest water level. For this reason, recovery tests may also be needed for non-pumping monitoring points which are affected by nearby pumping.

Ideally, water level measurements should be taken at times or locations unaffected by pumping. In particular, pumped leachate monitoring points should not be routinely used for leachate level monitoring unless there are no practical alternatives (such as providing new monitoring points remote from the leachate pumping points).

Where measurement of water levels in monitoring points affected by pumping is unavoidable (For example, in the vicinity of a major groundwater abstraction, or where leachate levels need to be maintained below compliance levels), a comment should be included in the monitoring records to indicate that pumping is being undertaken.

**Base level measurements in monitoring points**

Base level measurements can be used as a quality control check on the condition of a monitoring point. Measurement of base level should be made:

* At least annually as a maintenance check to ensure the screened interval remains unblocked.
* Whenever a monitoring point is recorded as “dry” or “blocked” a comparison can then be made with the constructed base elevation of the monitoring point and informed comment given on the significance of the absence of water and
* Whenever a monitoring point is recorded as “dry” or “blocked” a comparison can then be made with the constructed base elevation of the monitoring point and informed comment given on the significance of the absence of water.

In cases where base level measurement is likely to cause an unacceptable increase in suspended sediment in the borehole water, or requires removal of a dedicated pump, the measurement should be taken after sampling or between sampling events.

**Surface water level measurements**

Surface water levels should also be measured relative to ordnance datum to enable comparisons to be made between water bodies and with groundwater level measurements.

Equipment for surface water level measurements is relatively simple and includes:

* Fixed boards with scaled measurements.
* Electric tapes to measure depth to water from a fixed overhead datum point (e.g. from a bridge) and
* Levelling equipment (e.g. a surveyor’s level and staff) to record levels against a datum fixed adjacent to the water body.

### Surface water flow measurements

This group of measurements include:

* Surface water flow and
* Flows from discharge or abstraction points.

**Surface water flow**

Flow in rivers and streams can be estimated by:

* Direct measurement of velocity. Velocity can be measured using mechanical or electromagnetic current meters, tracers or even floats. Velocity is then converted to volumetric flow rate by multiplication by the cross-sectional area and
* Measurement of water level above weirs. A relationship can be developed between water level (stage) and flow, particularly upstream of a regularly shaped constriction, such as a v-shaped or rectangular weir. Once this ‘stage-discharge relationship’ is known, flow can be calculated from readings of water level.

The choice of appropriate method depends on the stream dimensions, flow rate, available fall, and tolerable uncertainty. Further guidance is provided by the Standing Committee of Analysts, 1996 and ISO 8363:1986.

**Flows from discharge or abstraction points**

Discharges may be fitted with integrating flow meters, in which flow measurement consists of timed readings of the meter.

When flow is emerging from a pipe or orifice, flow may sometimes be measured by timed filling of a container (bucket or drum and stopwatch). This method produces reliable results provided the container is large enough to hold at least 10 seconds’ flow. Health and safety considerations, particularly for contaminated discharges, may preclude use of this method, in which case recourse must generally be made to stream flow measurement methods.

Discharge measurements should be timed to take account of cyclic (e.g. daily) or rainfall dependent variations in flow.

## Collecting an appropriate water quality sample

### General sampling procedure

The general procedure for taking an appropriate sample of leachate, groundwater or surface water is given in the remainder of this chapter. Supplementary information is provided in Appendices 8 and 9 including a general sampling protocol and standard forms.

### Types of samples

Water samples taken for laboratory analysis (or analysed in the field) provide the simplest direct measurement of water quality. Samples are collected in a number of ways for different reasons and may be classified as:

* discrete samples which are taken at a single point in space and time (sometimes known as 'spot' samples). For example,:
  + - * A sample taken from a specific depth in a monitoring point and
      * A single sample taken almost instantaneously from a watercourse.
* Composite samples which originate from a number of locations or time intervals. For example,:
  + - * A sample collected after purging water from a monitoring point with a long, screened interval which spans several groundwater flow zones and
      * A sample formed by mixing a number of discrete samples such as stream samples taken at several specific time intervals.
* Continuous samples which are usually recorded by use of data loggers and electronic instrumentation: these types of samples are less commonly used for landfill monitoring.

The quality of surface water bodies can also be assessed indirectly by sampling sediment or living matter. Sample types include the following:

* Sediment samples from the base of surface water courses or ponds. Sediment readily absorbs and accumulates trace metals under normal pH and redox conditions. Analysis of trace metal concentrations from sediment samples can sometimes provide an indicator of the long-term accumulation of pollutants carried by a watercourse. This can be a better method of detecting pollution than simple spot sampling of flowing water and
* Biological assay of surface waters. Sometimes organisms present in water can be used to provide an overall indicator of water quality and the influence of external environmental impacts. Methods such as in situ toxicity tests or rapid assessments of indigenous biota can provide an early warning system of contamination and indicate the need for further chemical investigation. Spatial or temporal differences in biotic communities and investigations of individual organisms, e.g. bioaccumulation and biomagnification studies give a longer term assessment of the environmental impact of contaminants.

Further information on biological and sediment sampling methods is found in Standing Committee of Analysts, 1996. The remainder of this chapter provides guidance on the collection of water quality samples for chemical analysis.

### General requirements of sampling equipment

In order to obtain an appropriate water quality sample, any equipment used for taking samples should be:

* Clean and uncontaminated by previous samples prior to use at each monitoring point, or dedicated for use at individual monitoring points.
* Constructed of materials which will not significantly absorb or desorb substances which are to be analysed and
* Capable of transferring samples from the monitoring point to the sample container without causing any significant physical or chemical changes in water quality for the range of determinands to be analysed.

A review of equipment used to purge and sample monitoring points and for the collection of surface water samples is included in Appendix 10.

### Factors influencing water quality during sample collection

The quality of a water or leachate sample taken from a sub-surface monitoring point (and to a lesser extent from a surface water body) can be influenced by a number of factors, which are summarised in Table 9.1. The most important of these are the possibility of contamination due to poor monitoring point design and construction (Chapter 8), poor decontamination of sampling equipment (see Appendix 9 For example, protocol), unpurged water (Section 9.9) and the influence of sediment collected with sample water (Section 9.11). Other factors, such as type of sample equipment, sample containers, storage conditions and preservation methods can be important for specific analytes.

The remaining sections of this chapter provide guidance on practical measures which can be taken to minimise sources of error, to ensure that analytical results are as representative as possible of the water being sampled.

**Table 9.1: Processes influencing the quality of water samples from boreholes1**

| **Process** | **Sources** | **General comment** | **Analytes2**  **(A to F)** |
| --- | --- | --- | --- |
| Inappropriate sampling | Unpurged water standing in a borehole | Selection of most appropriate purging procedure to monitoring point is vital. | A, B, C, D, E, F |
| Cross- contamination | Sample equipment and handling | Equipment used for leachate and other contaminated waters should be segregated from that used for clean groundwaters and surface waters. | D, E, F |
| Aeration / oxidation | Sample collection | Contact with air can result in loss of dissolved gases and volatiles and lead to precipitation of some metals (e.g. iron as iron hydroxide). | C, D, F |
| Adsorption / dissolution of metals | Silt in water samples | Can be a problem for some trace metals, particularly iron, zinc and manganese. | D |
| Adsorption / desorption of organics | Materials in sampling borehole  Materials in sampling equipment | uPVC, nylon etc. can release trace organic substances from borehole lining and sample equipment.  Sampling equipment (including tubes and in-line filters) can affect contaminant concentrations, especially organics. | E  B, E |
| Pressure changes | Change in ambient pressure  Sample method | Gases and some trace volatile organics may be removed from solution.  Moving parts or surging by sampling equipment causes small pressure changes, which may release gases and volatile organics, cause chemical equilibrium changes, or disturb colloidal concentrations. | F  C, F |
| Temperature changes | Sample storage | Change between sample and analysis | F |

Based on Blakey et al. 1997, Section 3.5

1 This table only identifies influences from the sampling process. Additional influences in quality may occur in the handling and analysis of samples (see Section 9.11.6).

2 A: Major dissolved metals and phosphate.  
B: COD, BOD, TOC.  
C: Ammonia, oxidised-nitrogen, alkalinity.  
D: Trace metals.  
E: Trace organic compounds.  
F: DO, Eh, volatile organic compounds (VOCs) and dissolved gases.

## Collecting a sample of surface water

In collecting a surface water sample, the following procedure should be followed:

* Avoid collecting samples from the water surface wherever possible except where a floating product layer needs to be sampled separately. Submerge sample containers or transfer containers below the water surface to avoid collecting floating debris or other products. If this is not possible, solid materials should be removed from the transfer vessels before pouring into a sample container.
* Where information is required on floating products present on the water surface (e.g. oil or foam) it is necessary to collect two samples - one representative of the floating product layer and one of the sub-surface body of water.
* When collecting from ponds, lakes or wetlands, avoid collecting samples too close to the banks - a sample should be taken as far into the pond as is safe to collect, using an extension rod if necessary.
* When collecting from flowing watercourses avoid disturbing water upstream of the sample location. If possible stand downstream of the sample point and collect water into sample containers in the flow of water. It is preferable to sample direct into sample bottles to avoid cross contamination from sampling containers.
* Take samples from the fastest flowing part of the watercourse. Avoid stagnant parts of a watercourse and
* If determination of suspended solids in a stream is critical, it may be necessary to sample using a ‘flow-through’ sampling device.

Choice of sampling site is covered in Section 8.6. Where the sampling site is at a place where incomplete mixing has occurred[[15]](#footnote-15), two or more samples should be taken at different points across the width of the stream. These samples may be combined to form a composite sample, to give an indication of overall stream quality.

Surface water bodies are subject to cyclic and flow-related quality variations. For example, quality can vary between day and night, and between high and low flow conditions. This should be taken into consideration in deciding timing of sampling.

Further guidance on surface water sampling is given by the Standing Committee of Analysts, 1996 and ISO 5667 Parts 4 and 6.

## Unsaturated zone sampling

Sampling of pore water from the unsaturated zone requires the use of specialist sampling equipment. These are not considered in this document to be routine sampling methods applicable to most landfill sites. Background information and details of methods are provided in ISO 5667, Part 18 and ASTM standard D4696-92e1.

## Purging and sampling of monitoring points

### Preamble

Before commencement of sampling from sub-surface monitoring points, sampling objectives should be balanced against an understanding of the monitoring point design and its hydraulic properties.

Sampling objectives may be:

* To obtain a composite sample, i.e. a sample drawn from the entire screened or inflow depth of the monitoring point or
* To obtain a discrete or “spot” sample, i.e. a sample drawn from a specific depth within the screened or open section of the monitoring point.

Objectives may also relate to the volume of material from which groundwater or leachate is to be sampled. For example, sampling objectives may be:

* To obtain a composite sample which is sufficiently representative of water quality from a large volume of material surrounding the monitoring point i.e. pumping over a prolonged period would be required and
* To obtain a sample of groundwater from the strata immediately adjacent to the borehole or of leachate from waste immediately adjacent to the monitoring point, i.e. purging prior to sampling should not be prolonged.

It is often sufficient to know simply the sustainable pumping yield of a monitoring point in order to devise an effective sampling strategy (see following section). This information can be gathered during preliminary sampling programmes from which a long-term strategy can be developed.

### Purging of monitoring points

**Purging rationale**

Groundwater or leachate which remains in a monitoring point between sampling events can undergo significant chemical changes and may no longer be characteristic of water in the surrounding material. Processes that can alter the composition of standing water include interactions with construction materials, degassing and atmospheric contamination, biological activity, and contamination from dust or other extraneous materials that have entered the monitoring point. These processes can affect the pH, Eh (redox potential), DO (dissolved oxygen), alkalinity and electrical conductivity of the water in addition to the concentrations of dissolved ions and suspended solids. Leachates and leachate-contaminated groundwaters are chemically unstable in comparison with clean groundwaters. Their composition is generally complex and particularly liable to change if allowed to remain in contact with air for any substantial time between collection and analysis.

The selection of an appropriate purging procedure is dependent on many factors, including the type of sample to be collected (i.e. a composite or spot sample), the design of the monitoring point, aquifer or waste hydraulics and water chemistry. For example, in high permeability strata in a long-screened[[16]](#footnote-16) borehole in which the water level lies within the screened interval, purging may prove to be unnecessary. In situations where water is contained in a monitoring point above the screened interval, several times the volume of water in the monitoring point may need to be removed before an appropriate sample can be collected, or alternatively a low flow pumped sample may be appropriate. In low yielding strata, the only options may be to sample without purging, or to dewater the monitoring point completely and then take a sample during recovery.

**General purging guidance**

In the absence of any technical evidence to support a specific purging strategy for a particular monitoring point, the following guidance should be followed for leachate and groundwater sampling from sub-surface monitoring points:

* A purging trial should be undertaken to observe the behaviour of field determinands (e.g. conductivity, pH, temperature, or other determinands of interest), continuously or at intervals during purging. A sufficient volume (normally at least 3 borehole volumes) should be pumped during the trial to demonstrate genuine stabilisation of the pumped water chemistry. The results of the trial may then be used to determine a standard purge volume for the borehole.  
  A single “borehole volume” is defined as the volume of water contained within the lining of the monitoring point excluding the annulus. Calculated volumes for some typical lining diameters are shown in Table 9.2.
* In long-screened boreholes, an alternative purging strategy is to calculate the pumping time required to achieve a high proportion (say 95%) groundwater contribution to the pumped discharge.  
  This method requires a knowledge of formation permeability, and the use of formulae derived originally for test pumping of water supply boreholes (see For example, Gibb et al., 1981).
* In short-screened boreholes, an alternative is to purge three borehole volumes before sampling.  
  This approach may be used as a default standard for a borehole with a short screen and a water level above the top of screen.
* In the case of monitoring points which are dewatered before sufficient volume has been removed, two options are available.
* 1. Do not purge. Take a ‘grab’ sample using a depth sampler or bailer as appropriate. The water in the borehole should be disturbed as little as possible and
* 2. Dewater and then sample after allowing sufficient time for water levels to recover. The water level should recover to levels dependent on sampling objectives and the design of the monitoring point. The disturbance caused may affect some determinands, and the method is not recommended when samples are to be taken for volatile organics.

**Table 9.2: Standing water volumes in the lining of a monitoring point**

| **Lining diameter**  **(mm)** | **Water volume per metre depth (litres)**  **1 x borehole volume** | **Water volume per metre depth (litres)**  **3 x borehole volume** |
| --- | --- | --- |
| 17 | 0.2 | 0.7 |
| 20 | 0.3 | 0.9 |
| 25 | 0.5 | 1.5 |
| 50 | 2 | 6 |
| 100 | 8 | 24 |
| 150 | 18 | 53 |
| 200 | 31 | 94 |
| 250 | 49 | 147 |
| 300 | 71 | 212 |
| 500 | 196 | 589 |
| 1000 | 785 | 2356 |

Multiply the above volumes by the height of the water column in the borehole to obtain the total borehole volume.

Other purging strategies, particularly those involving purging lesser volumes of water (e.g. the use of a single purge volume for leachate monitoring points) would be acceptable where:

* Details of monitoring point construction are logged and presented in the site monitoring plan and either
* Trials have been undertaken to compare results from the proposed strategy with results from one of the default strategies given above or
* Where a number of monitoring points at the same site are very similar in design and environmental setting, it may be acceptable to carry out trials on a representative number of monitoring points, in order to develop a generalised purging strategy for similar monitoring points.

**Problems with purging**

Particular difficulties associated with purging include the following:

* In larger diameter or deep monitoring points, unless the monitoring point is being pumped for other reasons, it will often be difficult to purge even one borehole volume of water because of the large volume of water to be removed (Table 9.2) and
* In waste and fine-grained formations, purging can draw fines towards the monitoring point, which can enter the lining of the monitoring point and lead to a high suspended solids content in samples. This effect occurs particularly when the design of the screen and / or annular filter pack is not appropriate for the formation.

In these instances, a purging trial as described above should be carried out on at least one occasion. Future samples taken without purging should only be analysed for those determinands that remain unaltered (i.e. typically within a 15% variation). Where appropriate samples for determinands critical to assessment or compliance cannot be collected without purging, two options are available:

* Extended purging prior to sampling. i.e. for large diameter monitoring points: the use of a high purge rate over an extended period to obtain the necessary purge volume. For silting boreholes: the use of a low purge rate over an extended period, to avoid silting and
* Construction of a replacement monitoring point. The use of a more appropriate monitoring point design should help to overcome the problems encountered.

If, during purging trials, measurements fail to stabilise within three to five borehole volumes, consideration should be given to the cause of this. Possibilities include:

* Contamination derived from construction materials if these cannot be remedied, and determinands are critical, then a replacement monitoring point may be required
* Dependence of purge volume on purge rate in some cases reducing the purge rate may reduce the volume necessary to achieve stabilisation. However care is needed at lower purge rates to detect true stabilisation, as the process is slower.
* Instrument error readings may fail to stabilise due to instrument drift. This should be checked by adequate calibration procedures and
* Real variations in the water body For example, if the monitoring point is located near a boundary between waters of different quality (e.g. the margin of a pollution plume). In this case, purging strategy should be derived from a careful consideration of the monitoring objective.

Where analytical results from unpurged samples have not been correlated against purged samples, results should be treated with caution. Unpurged samples may be suitable for providing preliminary information for other purposes (e.g. prior to discharge to a treatment system).

**Collection and disposal of purge water**

Uncontaminated groundwater can usually be pumped onto ground surface or to a soakaway, drain or ditch during purging. An exception to this is when large volumes of water are removed over a prolonged period. In this case, SEPA should be informed in advance and their advice sought on the safe disposal of water. With contaminated groundwater or leachate, the choice of disposal option should be primarily governed by the need to minimise any health risks to monitoring or other personnel from unnecessary contact with contaminated purge water, and the need to avoid unnecessary cross-contamination of samples.

Options for disposal of contaminated groundwater or leachate (in order of preference) are as follows:

* Remove directly to a leachate / wastewater collection and disposal system. This is the preferred option for situations where leachate disposal systems are present on-site or for serious contamination of groundwater by List I or other dangerous substances.
* Dispose directly onto open areas of waste. This is feasible at operational landfill sites. The disposal area should be sufficiently remote from the sampling point to avoid the possibility of recirculation of purge water.
* For leachate monitoring points within a landfill, dispose within the waste body via a leachate monitoring point, abstraction well or purge water disposal point (see Section 8.4.3). This can be achieved by either pumping directly to the disposal point or by collecting in containers at ground surface (e.g. plastic bins) and then pumping or siphoning to disposal on completion of sampling. This is the preferred option for small diameter monitoring points where no alternative disposal facilities are available. However, the health and safety of personnel should not be compromised to achieve this.
* Collect in containers at ground surface for removal and suitable disposal. This option may be feasible for small purge volumes and
* Sample without purging. This option may be feasible where comparative trials have shown that the difference between purged and non-purged samples does not exceed the tolerable uncertainty of the determinands to be analysed and where there are no safe options for disposal of purge water.

### Purging and sampling equipment

Choice of equipment to purge and sample monitoring points is dependent on:

* The volume of water to be removed.
* The diameter of the monitoring point.
* The depth of pumping water level below ground and
* The requirement not to excessively alter sample quality.

The most common types used for groundwater and leachate are:

* Depth samplers, e.g. bailers and discrete depth samplers.
* Pumps, e.g. suction, peristaltic, inertial, electrical submersible pumps; gas lift pumps, bladder pumps and
* In-situ samplers dedicated or proprietary multi-level sampling systems using peristaltic, gas lift or inertial pumps to retrieve samples.

Further information on sampling equipment including advantages and disadvantages of each is included in Appendix 10.

## Field measurements of water quality

Measurements of water quality can be taken on site during sampling of monitoring points using a range of techniques including:

* Measurements using field instruments, For example, temperature, pH, electrical conductivity (EC), dissolved oxygen (DO), redox potential (Eh) and
* Measurements using chemical test kits and ion specific probes, For example, titration and colorimetric methods.

Field instruments can be used to conveniently monitor changes in water quality during purging of boreholes. They should also be used to obtain analyses of determinands that are liable to change in the time between sample collection and analysis at a laboratory. Where field measurements are taken for the latter purpose, measurements should be taken immediately prior to sample collection (and after purging). This data should then be carefully recorded for future comparison with laboratory measurements, in order to provide a record of changes in sample condition between field and laboratory. Examples of changes that can occur include:

* Change in pH due to loss of carbon dioxide from sample and
* Change in conductivity due to precipitation or dissolution of solids.

### Measurement using electronic meters and probes

Measurements of determinands such as pH, Eh, DO, EC and temperature are recorded using electronic meters and probes. All of these need calibration prior to use. Quality control records of calibration should be maintained for each individual instrument as part of normal field survey records. Specific issues arising from each field measurement are as follows:

* Eh should be measured in the field due to potentially rapid changes in the oxidation state of all waters during transport to laboratories. The measurement can be affected when the sample is exposed to the atmosphere, and should be taken in flowing water, a flow-through cell or using a downhole sonde during pumping. Measurements taken in beakers are unlikely to be appropriate. The use of any probes in oily environments (e.g. leachates) is problematical and Eh measurements are normally only undertaken on groundwaters and surface waters.
* The comments for Eh also apply to DO measurements taken in the field. As an alternative for relatively uncontaminated water, a sample can be fixed in the field, and analysed in a laboratory, using the Winkler method and
* Temperature, pH and EC are best recorded in flowing water, flow through cells or in down-hole sondes (during pumping if necessary), though reasonable measurements can also be obtained in beakers of standing water[[17]](#footnote-17). For routine monitoring purposes, analysis of pH and EC can reasonably be undertaken in the laboratory. Temperature should always be recorded in the field.

The use of down-hole sondes can, in some circumstances[[18]](#footnote-18), enable an appropriate measurement to be taken without the need for purging.

### Measurement using chemical test kits and ion specific probes

A number of proprietary test kits and ion specific probes are available for carrying out field measurements. These have obvious advantages in providing rapid analysis and can lead to improved management of water bodies at immediate risk from leachate egress in sensitive locations. The use of any field analytical measurements should always be accompanied by an approved calibration protocol and QC sampling procedure, which define the accuracy of the field method against comparative laboratory methods.

## Preparation and handling of water samples for laboratory analysis

### Consistency in sampling procedures

Sample handling procedures between the time a sample is removed from a monitoring point until it arrives at the laboratory need to be controlled. Decisions need to be made on matters such as:

* Whether or not suspended solids are to be included in the analysis.
* How samples should be preserved, if at all and
* Whether or not the sample containers and conditions during transport will significantly influence the quality of the sample.

Many of these issues are subject to ongoing technical debate and it is important that close liaison with laboratory is maintained when considering these issues. The guidance presented in the following section reflects the need for a flexible approach.

The most important feature in sampling is that of consistency. Once an acceptable strategy for sample handling has been adopted for a site, it should not be changed without good reason. If procedures used prove to be inappropriate, then it may be necessary to introduce a period of overlapping sampling programmes using the old and new procedures, to compare results and allow correlation with the historic data record. Without this overlap, elements of the entire historic data record for a site could be invalidated.

### Sample filtration

The decision as to whether to filter samples at the time of collection is not straightforward. Field filtration is not normally necessary for obtaining samples for organic analyses and is best avoided for this purpose. Samples for inorganic substances are normally filtered when dissolved rather than suspended or total forms of a substance are to be analysed (e.g. for metal concentrations or phosphates). Filtration may also be required to separate leachate or other waters from materials that may have entered the monitoring point accidentally. When groundwater monitoring boreholes are installed in clays and silts, purging can create a hydraulic gradient capable of carrying particulate matter into the borehole. If this is not removed by filtration, these soil particles can produce high levels of organic and inorganic analytes within the sample.

In surface waters (and some groundwaters) the suspended solids content is mobile, and filtration may not be appropriate. In leachates, suspended solids may be important in relation to the design of treatment or disposal systems, but it is the dissolved constituents that are more appropriate to understanding biodegradation processes and the potential impact from leachate egress.

If filtering is required, a choice must be made as to whether this should be carried out at the time of sampling, or in the laboratory. Changes, which may occur in an unfiltered sample due to the continued presence of suspended solids, introduce additional uncertainty to the final result.

This strategy assumes that field filtration is preferable in order to maintain consistency in sampling procedures and to minimise uncertainty in reported results. Where field filtration is not considered desirable, and the objective of sampling is to determine dissolved constituents, comparative analyses of field filtered and unfiltered samples should be undertaken. The difference between results for each analyte should then be compared with the tolerable uncertainty to determine the acceptability of the procedure.

Care must be given to the choice of filter used. Filters can add or remove dissolved components of the water. Filter media test documentation should be examined and QC sampling undertaken to evaluate these effects. Filter pore size can significantly affect results. Therefore standardisation is vital for all measurements for which comparison is required. Any assessment or compliance limits set for filtered determinands should include specification of the filter pore size.

Manufacturers’ instructions on filter use should be carefully followed. In particular, it is normally recommended that a minimum volume of sample water should be passed through the filter and discarded prior to sample collection, in order to reduce the effects of sample alteration by the filter.

The addition of preservatives to “fix” dissolved constituents in samples prior to analysis should only be undertaken on filtered samples. Ideally, filtration should be carried out using in-line filters and under pressure rather than vacuum.

### Sample preservation

Biological and chemical processes may occur in water samples with sufficient rapidity to significantly modify some components of the sample chemistry within a few hours (or even minutes) of sampling. Details of maximum delay before analysis for specific analytes are given by the Standing Committee of Analysts. Constituents that are critical for assessment purposes may need to be preserved in the field prior to submission to a laboratory, depending on feasible delivery times. Where preservation is undertaken on-site, this should be planned alongside the chosen filtration strategy. Preservation of samples can be undertaken by one or more of the following methods:

* Using chemical preservatives. The preparation of sample bottles with chemical preservatives should always be undertaken by the laboratory responsible for analyses. The analyst should always be consulted, particularly when planning surveys requiring field preservation, and a procedure agreed in advance. This should be incorporated into the site control and monitoring plan and
* By maintaining samples at low temperatures. Many determinands will remain stable for several days after sampling as long as they are stored at low temperature. Ideally, and in critical cases, the temperature should be between 2 and 4°C, requiring the use of portable fridges. Cool boxes with freezer packs can be used to achieve a temperature of about 12°C, which may be sufficient for short periods while samples are transported to the laboratory. Unfiltered and unpreserved samples should as a minimum be cooled, and should be submitted to a laboratory within 24 hours of sampling.

### Selecting and filling sample containers

The choice of sample container may have important implications for sample stability and the prevention of contamination from, or adsorption onto, the container wall. The sample bottle will usually need to be prepared for sampling prior to fieldwork and the type of bottles used should be agreed in consultation with the analytical laboratory. Ideally, the laboratory should supply appropriate containers for sampling.

All containers used for sampling should be leak-proof. Typical material types are given below:

* Glass bottles. Preferred for most organic determinands, dissolved gas and isotope analyses. Amber glass reduces photochemical reactions. A smooth rigid bottle is important when sampling dissolved gases and trace organics to prevent the trapping of atmospheric gases during sample collection. Glass bottles should contain an inert seal such as polytetraflouroethene (PTFE) in the cap.
* Polyethylene terphthalate (PET) bottles of food grade standard. Usually chosen for inorganic analyses and organic indicator analyses such as TOC and COD and
* Polyethylene and polypropylene containers. Used for most inorganic analyses. They are light, robust and inexpensive and can be supplied with wide necks for easy filling.

In general, containers should be filled to the brim to avoid the inclusion of air in the sample (unless there is a ‘fill-to’ mark, For example, in pre-preserved bottles). Further guidance on containers and filling requirements is provided by the Standing Committee of Analysts, 1996.

### Sample labelling

Labelling should either be carried out in advance, or immediately after sampling. As a minimum, samples labels should carry the following information:

* Unique monitoring point reference.
* Depth of sample (where appropriate).
* Sampling date and time and
* Sampler identification.

### Sample storage and transportation

Care should be taken to ensure that no appreciable contamination of the samples occurs during storage after sampling, and during transportation back to the laboratory facility. The main factors affecting sample stability are time of storage, temperature, light and pressure changes:

* Samples should be delivered to the laboratory as soon as possible after sampling - ideally on the same day and preferably within 24 hours of sampling.
* Samples should be exposed to minimum light by storage in a covered box.
* The samples should always be stored at a lower temperature than that at which they were sampled and preferably in an insulated cool box with freezer-packs, or in a fridge. This is particularly important for those samples that have not been chemically preserved.
* Samples should be packed to avoid movement and breakage during transport.
* Highly contaminated samples such as leachate should be stored separately from relatively clean water samples.
* Agitation of the sample during transport can encourage some of the chemical processes, particularly if the sample has a high suspended solids content, or includes air. In most cases these chemical changes will be insignificant, but for some trace or volatile analytes differences could be significant. In some cases, specific QC effort may be needed to quantify handling and storage effects and
* Health and safety arrangements for handling and transport of samples should be established with monitoring personnel, the courier and the receiving laboratory.

## Laboratory analyses

### Preamble

Close liaison with analytical laboratories, whether these are in-house or at external facilities, is vital to ensure consistency in sample handling and the production of appropriate analytical data. Laboratory personnel need to be familiar with the analytical objectives of the monitoring programme, whilst sampling personnel should be aware of the issues affecting analytical accuracy. The following sub-sections provide guidance on:

* Laboratory accreditation and
* Laboratory procedures to be agreed (i.e. sample handling, analysis and reporting).

### Laboratory selection, contract and accreditation

The performance standards required of the laboratory are determined by the monitoring objectives, tolerable uncertainty, and Agency requirements. These should be conveyed to the laboratory and incorporated into any contract made.

The laboratory should have a documented procedure and performance specification for each analysis confirming that it is appropriate for the purpose required. This should include specification of the matrix (clean water, contaminated water, leachate) for which the analytical method is designed.

The laboratory should have a quality manual, which details policies covering at least all the remaining sections of this chapter (9.12 to 9.14 inclusive).

Ideally, the quality manual should describe the following:

* The quality policy.
* The quality system.
* Organisation and management.
* Auditing and review arrangement.
* Equipment.
* Calibration.
* Analytical methods.
* Sample handling.
* Records.
* Analytical reports.
* Sub-contracting.
* Complaints and queries and
* An analytical quality control procedure.

Preferably, the laboratory chosen should operate a quality management system of at least the standard demanded by the United Kingdom Accreditation Service (UKAS). The advantage of using accredited laboratories is that the accreditation body will carry out audits to prove that the laboratory is conforming to the standard agreed in the contract with the operator.

Most of the requirements outlined in this sub-section would be met by a laboratory that is certified to BS EN ISO 9001 or 17025.

### Sample handling, analysis and reporting

Procedures for handling and preparing samples are critical and can significantly influence the final analytical results of a number of key determinands (e.g. dissolved metals, COD, BOD, TOC). The following procedures should be agreed in writing with the laboratory and included in the site control and monitoring plan:

* Sample reception and registration arrangements for samples delivered / documentation to be exchanged with laboratory to preserve chain of custody / special arrangements for out of hours delivery if appropriate.
* Arrangements for continued preservation of samples, e.g. refrigeration of samples delivered in cool boxes.
* Sample preparation and preservation procedures, a specification of sample preparation and preservation methods for each analyte and matrix should be produced. Procedures will vary depending on whether filtration and preservation has been carried out in the field or is to be undertaken in the laboratory.
* Analytical methods, a specification of analytical methods should be agreed with the laboratory. Where non-standard methods are used these should be documented, particularly if analyses are submitted to other laboratories. Further detail on the specification of analytical methods is provided in Appendix 12.
* Reporting requirements, this will include specification of the information required in reports, reporting times, and format of digital and tabulated data and
* Quality control information to be reported, all laboratories operate a variety of internal and third-party quality control methods and those to be reported should be agreed in advance.

## Quality control sampling

### Introduction

The collection and analysis of quality control (QC) samples provides a means to determine whether or not sampling or analytical procedures have significantly affected analytical results. An effective QC sampling programme is an essential part of quality assurance. Without it, it may not be possible to distinguish whether monitoring is measuring real changes in the water system or simply recording variations caused by sampling and analytical procedures. This particularly applies to constituents of water which could be gained from sources unrelated to the sampled water or lost from the sample during handling and transit.

This section provides general guidance on determining the number and types of QC samples required at different stages in monitoring programmes. Further details are provided in Appendix 11.

### Types of error: accuracy and precision

Each stage of the monitoring process, from monitoring point construction through sampling, handling and analysis to final reporting of results, can introduce errors of two kinds.

* Errors arising from random variation. These arise from variations in the behaviour of the sampling and measurement systems. These variations may or may not be evenly distributed around the actual measurement value. When such errors / variations are small relative to the measurement value, precision will be high and
* Systematic errors (biases). These are variations which consistently bias the measurement in one particular direction (e.g. increased concentrations of substances caused by cross-contamination, or loss of substances induced by volatilisation during sampling). It is rarely possible to determine all sources of bias. It may be possible, through inter-laboratory comparisons, to evaluate relative bias between laboratories. Likewise, comparisons between field and laboratory analyses can be made. If systematic errors are small, then the mean of a sufficient number of samples will be close to the true mean (i.e. accurate).

For an individual sample, accuracy is good when both random and systematic errors are small.

The error arising from random fluctuations can be measured by appropriate replications of both sampling and measurement processes. Bias is difficult to estimate in absolute terms, as there is no satisfactory way of finding the “true” value. However individual sources of bias can be investigated by the use of standards of known (or zero) measurement value.

Both systematic and random errors can be reduced to some extent by the use of carefully designed, standardised sampling and measurement protocols as described earlier in this chapter (see Section 9.4). However, some errors will remain, and it is the function of QC sampling to evaluate these.

### Determining the number of QC samples

The number of QC samples to be collected during a sampling survey will depend on the following:

* The measurements (analyses) being made. Those which are susceptible to effects relating to sampling, sample handling, sub-sampling and sample preservation / storage (e.g. pH, ammonia, trace metals, volatile or semi-volatile organic compounds) may require a greater QC effort. Analyses that are more difficult to undertake will require greater analytical QC.
* The number of water samples to be taken. At the outset of a monitoring programme, or where monitoring procedures are significantly changed, QC samples should make up at least 10% of the total number of samples taken on each survey. For complex sampling (e.g. characterisation of trace concentrations of volatile organic compounds), a greater proportion of different types of QC samples would be expected and
* The maturity of the monitoring programme. The QC effort should be greatest at the outset of a monitoring programme. Once procedures have been established, and quality control has shown that procedures are under control, relaxation of the proportion of QC samples would be reasonable.

### Types of QC sample

Each stage of the sampling, handling and analysis process introduces errors. Distinguishing the contribution to total error from each individual source requires a substantial number of different types of QC sample (see For example, ISO 5667 Part 14 (1998) for sampling, and ISO 13530 (1997) for analysis). The approach recommended in this guidance is to use QC sampling to determine overall errors initially. If these are unacceptable, then more detailed QC sampling is required to locate the sources of the errors.

Standard laboratory practice incorporates QC procedures to distinguish errors arising from the analytical process. For routine sampling surveys the QC sampling effort should consist of the following three types of QC sample:

* Sampling duplicates. These are a means of quantifying errors arising from random variations in the entire sampling and analytical process. Sampling duplicates should ideally be taken following the main survey sample, after repeating the entire sampling process (including purging wherever practicable).
* Field standards. These are a means of quantifying both systematic and random errors for selected analytes arising as a result of the sample handling and analysis process (i.e. excluding the sample collection process). Field standards are laboratory prepared water samples containing a known concentration of specific analytes. A standard sample for each relevant analyte is passed through the same sampling equipment used to collect the main survey samples (as far as practical), and thereafter treated in exactly the same way as the main samples. An analysis of the QC sample can then be compared to the known standard concentration. This procedure will detect both gains and losses of analyte, and is particularly relevant for analytes such as ammoniacal-nitrogen, trace metals, TOC and volatile organics and
* Field blanks. These are used to detect systematic and random gains (but not losses) over an entire analytical suite. Field blanks are a form of field standard, consisting of a laboratory prepared sample of pure water, which is treated in the same way as described for a field standard above. This QC sample is then analysed for the same suite as the main survey samples.

Other QC samples may be needed to justify the choice of a specific sampling procedure. For example,:

* Where laboratory filtering is used routinely, occasional field filtered samples should be analysed for comparison or
* Where samples have been proven to be acceptable without purging by comparative trials and a no-purge sampling protocol is routinely used, the collection of occasional purged samples may be appropriate.

If the sampling and measurement errors estimated from any of the above QC samples are excessive in relation to the tolerable uncertainty (Section 6.3.5) then:

* Further QC sampling should be introduced to identify the sources of errors in the sampling and analytical process or

if a specific part of the process can be identified as the major source of error:

* Modify this specific part of the sampling or analytical protocol.

### Strategy for determining QC effort

QC effort should ideally be concentrated during the period of initial characterisation monitoring, so that the major sources of error in the sampling process are eliminated as soon as possible in a monitoring programme. Routine monitoring surveys can then be carried out with less intensive QC effort.

For more sensitive analyses (e.g. volatile organic compounds) additional types and quantities of QC samples will be needed:

* QC samples need to be taken for each sampling protocol; i.e. separate QC samples are needed for leachate, groundwater and surface water sampling procedures[[19]](#footnote-19).
* At the commencement of a new monitoring programme, or if sampling procedures are changed, at least 10% (and a minimum 4 per sampling protocol) of all samples analysed from a monitoring survey should be accompanied by QC samples (sampling duplicates, field standards and field blanks).
* Standard samples need only be used for specific indicator parameters that are liable to be affected by sample collection, transport and storage procedures. For routine sampling surveys at biodegradable sites, this should include ammoniacal-nitrogen and TOC. Other standards for trace constituents may be required where these are defined in the site control and monitoring plan as being key indicators for monitoring purposes and
* QC samples can be reduced to a minimum of 5% of samples if an evaluation of QC results after the initial characterisation period shows the total sampling and measurement error to be within acceptable margins (in relation to the tolerable uncertainty).
* If an evaluation of QC results after four consecutive surveys of 5% QC sampling shows the sampling and measurement errors to be within acceptable margins, then QC sampling can be reduced to an occasional basis for indicator measurements. All ongoing characterisation monitoring should include at least 5% QC samples.
* In circumstances where excessive sampling and measurement errors are persistent, other types of QC sample should be introduced to identify and remove the cause (see ISO 5667 Part 14) and
* Once a QC sampling programme has matured, results should be routinely reviewed both during validation checks following each survey and more critically on an annual basis (Chapter 10). Where persistent sampling and measurement errors are identified the proportion of QC samples should be increased until the cause is identified and removed.

### Reporting of QC sample analyses

Field QC sample analyses should be processed by the laboratory in the same way as all other samples. The laboratory should not be able to identify any sampling duplicates. The responsibility for reviewing the significance of these results lies with the person responsible for the sampling programme.

On receipt of analytical results from the laboratory all QC sample results should be isolated from and dealt with separately from other monitoring data. QC results should be clearly identified in any paper or computer records to avoid confusion with routine monitoring data.

The results of an effective QC sampling programme will ensure that:

* Mistakes and spurious data can be traced.
* Measures can be set in motion to deal with unacceptable sampling and analysis errors.
* The validity of the data can be substantiated and
* The sampling and measurement uncertainty (error) can be quoted with results.

Procedures for data handling and reporting are outlined in Chapter 10.

## Documentation

The responsibility for ensuring that the correct procedures are followed for sample collection, preservation, handling and analysis should be clearly defined in the site monitoring or environmental management plan. The documentation of all procedures in the field and laboratory is of vital importance, so that the entire monitoring process can be audited.

Examples of forms for documenting field methods and chain of custody of samples are included in Appendix 8.

### Field records

Paper records should be maintained which document the following procedures:

* Field equipment calibration.
* Purging of monitoring points.
* Sample observations and
* Field instrumentation measurements.

### Laboratory submission records

Each bottle submitted to a laboratory should be uniquely labelled in a form agreed with the analytical laboratory (some laboratories will provide bottles with pre-printed labels). Documents submitted to the analytical laboratory should include:

* Sample analysis instructions form and
* A chain of custody form.

# Monitoring Locations and Schedules

## Introduction

This chapter describes the principles underlining the control and interpretation of data generated by landfill monitoring programmes. There are a number of management tasks involved with data and for which guidance is provided under the following headings:

* Section 10.2: Data management principles.
* Section 10.3: Quality control.
* Section 10.4: Data collection.
* Section 10.5: Collation of monitoring data and preliminary storage.
* Section 10.6: Data validation.
* Section 10.7: Data storage and archiving.
* Section 10.8: Data presentation, review and interpretation and
* Section 10.9: Reporting.

Although focusing on monitoring of leachate, groundwater and surface water, the guidance given in this chapter has application to other environmental monitoring programmes.

## Data management principles

### General principles

A monitoring programme at a small-scale landfill operation may generate only modest volumes of data which can be kept on paper or simple computer records and submitted to SEPA in total. Data from many biodegradable or larger-scale landfill operations may need to be collected from a number of monitoring points over many decades. There is a need to effectively control and maintain an accurate and reliable long-term data record. Data handling and reporting for these sites are important issues.

Data held in a data management and reporting system should be:

* Quality assured:
  + - * Raw data must be preserved.
      * Integrity of data must be preserved as it is processed.
      * Data quality must be checked and the results of quality checks fed back into the monitoring programme and
      * The system must enable auditing to trace sources of data back to original records.
* Logically collated:
  + - * Data must be stored in a form which can be readily manipulated for interpretative purposes and
      * Systems need to be in place that can efficiently collate data to meet the requirements of response times incorporated into assessment criteria, and reporting dates agreed with SEPA.

## Quality assurance

Monitoring forms part of the overall quality control check on the performance of a landfill against its design specification. Costly or far-reaching management or regulatory decisions may rely on monitoring data, and accordingly the need for reliable data cannot be overstated. Quality Assurance is achieved by:

* Stating quality objectives in the site control and monitoring plan.
* Stating and implementing Quality Control (QC) measures which achieve the objectives and
* Documenting the results of QC checks, to preserve evidence of data quality.

### Stating quality objectives

Quality objectives (such as specifying the tolerable uncertainty of monitoring measurements - Section 6.3.5) should be an integral part of the overall monitoring programme objectives given in the site control and monitoring plan.

For larger sites, or companies operating several sites, it may be appropriate to document quality assurance procedures within a separate quality assurance plan.

### Achieving quality control

Adherence to good quality control practices will improve confidence in presented data. Quality control of monitoring data is accomplished in two ways:

* Minimisation of uncertainty at the time of measurement and sampling. This is achieved by appropriate monitoring programme design, and standardised good practice in data collection and handling (i.e. by the adoption of sampling and handling protocols) and
* Estimation of sampling and measurement uncertainty at the time of reviewing results of measurements. This is achieved by an assessment of QC samples and by checking monitoring data.

### Documenting quality control

All quality control checks should be documented within routine survey reports (Section 10.9). Where changes to records are necessary, an audit trail documenting the rationale and steps taken in reaching this conclusion should be maintained.

## Data collection

In the context of the overall quality management of data, the quality of data collection can be managed by:

* The use of competent personnel staff - should be trained and familiar with data gathering, its use and application.
* The use of sampling and handling protocols to ensure care and consistency in methods used - protocols will include provision for QC sampling to provide a check on quality of sampling and handling procedures.
* The use of standardised recording procedures - e.g. checklists and forms for data entry, including procedures for documenting data gathered using automated logging equipment and
* The use of accredited (e.g. UKAS) and quality assured laboratory analyses - The use of accredited procedures does not always guarantee competence in analyses. Clarification on methodology and matrix covered by any accreditation procedure should always be sought from laboratories, particularly when analysing for leachate.

## Collation of monitoring data and preliminary storage

### Types of data

Data collation is the process of gathering and ordering incoming data into a format suitable for preliminary storage. Where incoming data are in electronic form, a paper copy of the unprocessed data should always be kept available for reference.

Data arising from monitoring programmes include:

* Data related to monitoring infrastructure, compliance and other standards - e.g. monitoring point construction details, site details, assessment and compliance standards, environmental quality standards. These data may not change with each monitoring survey, but are nonetheless required whenever ongoing monitoring data are reviewed, and should be readily available for this purpose and
* Data related to specific monitoring surveys - e.g. field and laboratory measurements and records, chain of custody records, observational notes.

### Preliminary data entry and storage

Data can be stored using either paper or computer systems. Whichever is used, the process of preliminary storage must include:

* A system for cross-referencing all transcribed data to original field records or laboratory certificates.
* A means of indicating where data have been altered or omitted. Examples where this sometimes occurs include comments, numeric data with varying numbers of decimal places (reflecting varying analytical precision), or determinations which are less than detection limit[[20]](#footnote-20).
* A means of indicating whether or not data have been validated and
* Archiving of all original field, laboratory and other relevant paper records.

Personnel responsible for data collation should be familiar with the site monitoring or environmental management plan (preferably having visited the site and its monitoring facilities).

## Data validation

### Preamble

Data validation involves checking data for simple errors and inconsistencies and remedying these wherever possible. This should be followed up by acting to reduce the chance of similar errors occurring again.

Validation rules must be formulated with care to avoid rejection of data which, though extreme, are not erroneous. This particularly applies where validation rules are incorporated within computerised systems.

The person responsible for data validation should have an understanding of the meaning of the data and have access to the following records:

* The newly entered data, including records of validation rule breaches recorded during data collation and preliminary storage.
* The original data records.
* All historic monitoring data and
* The site control and monitoring plan.

### Validation checks

There are a number of simple validation checks that can be carried out on data. These include:

* Internal data checks applying - tests to a suite of data collected from a single monitoring point from one specific monitoring survey and
* External data checks - applying tests by comparison to other related data.

Specific validation checks include:

**Internal data checks:**

* Simpleerrors - e.g. transcription errors, incorrect sample identification, missing data.
* Logical checks - e.g. data outside valid range and
* Chemical or biological data checks - e.g. chemical ratio checks, major ion balance calculation, field/lab comparisons.

**External checks**

* Comparison with quality control sample analyses.
* Comparison with historic analyses from the same monitoring point.
* Comparison with analyses from similar monitoring points and
* Evaluation of other sample attributes; e.g. adherence to sampling and handling protocols, any notable departures from normal procedure.

### Handling anomalous or erroneous data

Where anomalous or erroneous data are identified these should be dealt with by:

* Confirming values against original field records or laboratory certificates
* Referring unresolved queries to the laboratory or field monitoring personnel and
* Undertaking repeat measurement or analysis.

A written record of the above procedures should be maintained. It may not always be possible to carry out repeat analyses or measurements due to the time delay between collection and collation of results. However, where questionable data have been identified which are important for compliance or critical to the performance of the landfill, repeat sampling should be undertaken immediately.

If erroneous or questionable data remain on file after inquiry, they should be treated as follows:

* Data identified as questionable should be included on the data record for the site but flagged with an explanatory comment.
* Data, which are demonstrably erroneous, should be removed from the validated data record for the site. The empty record should be flagged with reference to the validation record and include an explanatory comment and
* If data are identified as erroneous after being submitted to SEPA, formal notification should be given in writing to SEPA along with a technical justification for removing or amending the erroneous data from file records and the public register.

## Storage and archiving of validated data

Working data that has been validated should be stored in a permanent but accessible location, where it is available for regular review. Validated data should be clearly distinguished from data that is not yet quality assured. This distinction may be achieved by transfer of data to separate permanent storage, or it may be achieved by flagging the data and retaining it in the same storage location.

The likely duration of the monitoring programme should be taken into account when specifying storage and archiving facilities. Data will have to be stored for the lifetime of the site, which may be many decades. Data should be appropriately ordered and handled to ensure its survival for at least this length of time.

Where data are stored on computer, they should be regularly backed up and back-up media stored in a secure place. Additionally, a paper copy of all validated data should be produced for long term storage to allow for the possibility of degradation or loss of electronic archive media. Archived paper copies of validated data should be distinguishable from the unvalidated source data.

## Data presentation, review and interpretation

### Introduction

Following validation and storage, monitoring data must be periodically evaluated against:

* Compliance conditions - failure to meet a compliance condition in the site permit (e.g. a maximum leachate level) may lead to prosecution.
* Assessment criteria - breach of assessment criteria e.g. a groundwater control level, should be addressed by the implementation of appropriate contingency measures within the specified response time and
* Monitoring programme objectives - failure to meet a monitoring programme objective (e.g. the number of monitoring points becomes insufficient due to damage) should be addressed by implementing measures to achieve the objectives.

### Data presentation

The exact format of data reported from the data management system is dependent on the volume of data generated by monitoring programmes, and their application. In general, data should be presented in simple tabular format accompanied by graphical representation where this aids in understanding information.

Specific information requirements to be provided from monitoring programmes are as follows:

* Monitoring performance summaries:
  + - * To compare actual monitoring tasks undertaken against those planned and
      * To summarise results of quality control checks, highlighting where quality problems have arisen and any conclusions which can be drawn from such checks.
* Leachate monitoring data
  + - * To present leachate level data relative to Ordnance Datum and relative to the base of the site (data for individual cells should be grouped together and include reference to cell base levels, and assessment and compliance levels where these are established) and
      * To present leachate quality data (data for individual cells should be grouped with reference to any assessment limits).
* Groundwater monitoring data:
  + - * To present groundwater levels relative to Ordnance Datum (data for each separate groundwater body should be grouped together) and
      * To present groundwater quality data (data for separate groundwater systems should be grouped together with reference to control and trigger levels).
* Surface water monitoring data:
  + - * To present surface water level and flow data (data should be grouped by sub-catchment and, where appropriate, compared to rainfall data) and
      * o present surface water quality data (data should be grouped by subcatchment, with upstream and downstream monitor points clearly indicated, together with reference to any established compliance limits or assessment criteria).
* Consented discharge points:
  + - * Show relevant results of monitoring of any consented discharges or other contaminant sources, with reference to consented limits.

In each case, consideration should be given as to whether the monitoring is providing appropriate data which meet the objectives of the monitoring programme they are designed to satisfy.

Data prepared by operators for submission to external parties (e.g. SEPA, or an outside specialist) are often presented in summary tables. However, data presented in this form will rarely meet the criteria outlined above, except for sites with limited monitoring and low volumes of data. Summary data can often be prepared more effectively in graphical format. Formats which are particularly encouraged include the following:

* Time series charts: Plotting data as a time series enables trends to be visualised and compared and may allow a degree of prediction based on extrapolation of trend lines. Inclusion of control data (such as maximum leachate level, base level of cell, assessment and compliance limits) can add further value to the charts.
* Further interpretation of time-series charts (particularly in relation to assessment criteria) can be provided by the presentation of control or cusum charts and
* Spatial plots: Where the spatial distribution of data is significant (mainly for groundwater level and quality data), the use of spatial plots is encouraged. An important use is to demonstrate the location and extent of groundwater contamination. For operations involving large volumes of spatially related data, the use of geographical information systems (GIS) may be appropriate.

Guidance on other interpretative graphical methods can be found in standard texts[[21]](#footnote-21).

### Data review and interpretation

A number of specific review tasks should be implemented on validated data:

* Comparison of actual against specified monitoring schedules. Any missing data should be identified with comments and recommendations for retrieving this information in future surveys (e.g. a replacement monitoring point may be needed).
* Evaluate significance of QC data. This will include a periodic assessment of laboratory and field QC data to determine whether data quality meets the monitoring programme objectives. Both quantitative and qualitative QC data may be presented in tabular or graphical form in order to assist in this task.
* Application of assessment tests. Assessment criteria response times will dictate the maximum duration of the period between monitoring and review, but it is to the operator’s advantage to review data speedily in order to provide the earliest possible warning of any difficulties and
* A review of the current understanding of the hydrology and hydrogeology of the site. To ensure that monitoring objectives are still being met in the light of this understanding. For example, it may emerge from data that groundwater flow direction is not the same as it was thought to be at the time of site investigation, so that alternative or new down-gradient monitoring boreholes may need to be provided.

## Reporting

### Introduction

Section 16 of the Landfill Regulations states that ‘the operator shall report to SEPA on the basis of aggregated data (a) on its request; and (b) in any event at least once a year, the results of monitoring and on such matters which SEPA requires to demonstrate compliance with the conditions of the landfill permit or to increase knowledge of the behaviour of waste in landfill’

Wherever possible, data records should be provided to SEPA electronically in a format agreed between the site operator and SEPA. All reporting should be succinct, backed up by necessary and sufficient data, which should be quality assured and appropriately presented. In particular, data and reports submitted to SEPA should be:

* Submitted on time - timescales may be stipulated by permit condition, although in all cases timely submission of data and reports is essential to ensure informed discussion of its significance before any action is taken.
* Quality assured - any erroneous data submitted to SEPA can lead to unnecessary, time consuming and costly exchanges.
* Collated and presented in a consistent format - whilst the detailed format of data submitted will vary from site to site and for different types of data, simple tabular and time-series or control chart graphical summaries are preferred with clear comparisons with any established compliance limits or assessment criteria and
* Accompanied periodically by interpreted reports - the content and layout of reports should be standardised in a format agreed between the operator and SEPA to highlight key issues of compliance or departures from baseline conditions. The frequency of reporting should be related to pathway travel times or anticipated rate of change of concentration (e.g. immediate report of surface water contamination vs. annual summary of leachate quality).

### Reporting tasks

The format and type of monitoring reports will vary depending on the complexity of monitoring programmes. Typically, the following types of reports can be used:

* Notification reports - these are issued to provide notice of a breach of assessment criteria or compliance conditions, or other potential or actual polluting incidents. The report should include notification of the contingency measures required or implemented.
* Routine survey documentation - these are prepared primarily to provide detail and comment on results from individual monitoring surveys. These reports include quality control and validation records and any changes made to data as a result of these procedures.
* Compliance reports - these are prepared for submission to SEPA to include data and comment relating primarily to compliance with permit conditions and
* Review and data submission reports - these are prepared to periodically assess all monitoring results to date against the monitoring objectives for the site. In most cases, these reports should form the principle means of collating and submitting routine monitoring data to SEPA.

### Notification reports

Notification reports should be seen as the prime means of disseminating information for which action is required by site management and / or SEPA. Notification reports should be issued when breaches in assessment criteria or compliance limits have occurred or if any other potential or actual instances of pollution arise from the landfill. These reports should provide clear, concise information and carry a recommendation for action (or advise of action taken). Timescales for issuing reports may be specified by permit condition, but in all cases reports should be issued within a time frame agreed between the operator and SEPA. Reports should be issued to both site management and SEPA and should include:

* Date and time of issue of report;
* Name, position and contact information for person issuing report;
* Date and time of monitoring surveys or observations confirming the breach of a compliance limit or assessment criterion, or an actual pollution incident.
* Pollution incident recorded or assessment criteria breached (referenced to relevant section of the site control and monitoring plan).
* Contingency action required or implemented and
* An indication of the urgency of response needed by management and / or SEPA.

Attached to the report should be other information that helps clarify the seriousness of the incident. For example,:

* A tabular summary of relevant data.
* A time-series graph of data including assessment and compliance limits and
* Any other relevant observations.

In instances where assessment criteria or compliance limits are regularly breached and action is being implemented by the site operator (e.g. where leachate level control measures are underway or where the source of contamination to groundwater is being investigated), alternative ongoing reporting procedures should be agreed between the site operator SEPA to avoid unnecessary duplication of notification reports.

**Table 10.1: Example schedule of reporting tasks**

| **Report and content** | **Timescale for reporting to:**  **Site management** | **Timescale for reporting to:**  **SEPA** |
| --- | --- | --- |
| Notification reports:  Breaches of assessment criteria;  Contingency implemented. | Within response time specified in assessment criteria. | Within response time specified in assessment criteria. |
| Routine survey documentation:  Quality control and data validation records.  Tabulated results; comment on breaches of assessment criteria.  Comment on unusual or notable data.  Changes needed to monitoring infrastructure or procedures. | Before next routine survey | Not normally required but must be available for inspection. |
| Compliance reports:  Details of compliance and assessment monitoring programmes.  Tabulated compliance and assessment data.  Comment on breaches of assessment criteria, and action taken.  Changes needed to monitoring infrastructure or procedures. | At least quarterly for sites posing high risks to receptors and at other intervals to be agreed between SEPA and Site Operator.  (NB: Any changes to monitoring infrastructure or infrastructure or procedures should be agreed with SEPA prior to implementation). | At least quarterly for sites posing high risks to receptors and at other intervals to be agreed between SEPA and Site Operator.  (NB: Any changes to monitoring infrastructure or infrastructure or procedures should be agreed with SEPA prior to implementation). |
| Review reports:  Review of site development and monitoring infrastructure changes since last report.  Review of changes to risk assessment and site monitoring plan since last report; review of monitoring programmes completed against planned schedules.  Collation of monitoring data.  Review of monitoring data.  Conclusions and recommendations. | Annually | Annually – to be submitted within 3 months of end of reporting year. |
| Site control and monitoring plan: see Chapter 5 for contents. | Annually during operational stage - to be submitted  within 6 months of the end of the reporting year to  SEPA.  As necessary following restoration, with a minimum  review interval of 5 years. | Annually during operational stage - to be submitted  within 6 months of the end of the reporting year to  SEPA.  As necessary following restoration, with a minimum  review interval of 5 years. |
| Risk-based monitoring assessment. | As necessary following breaches of assessment criteria. | As necessary following breaches of assessment criteria. |

### Routine survey documentation

Routine survey documentation is primarily concerned with conveying to site management, confirmation of work undertaken, results obtained and the quality of results. Whether this information is compiled into a formal report, or is simply collated for internal review, is a matter for the operator and will typically be dependent on the size of the organisation. Whichever method is adopted, the documentation must be available for inspection by SEPA on request.

The documentation will include:

* Survey results - summarised in tables.
* Details of data validation - documentation and comment on QC tests and breaches and any actions taken to remedy them; recommendations for ensuring excessive errors identified by QC are not repeated and
* Comment on any breaches in assessment or compliance criteria - including a statement of any assessment or contingency actions undertaken or recommendations for such action.

### Compliance reports

Compliance reports are the formal means of submitting routine compliance data, required by permit conditions, to SEPA.

For sites posing low risk, the function of compliance reports may be fulfilled by annual review reports (see next section). For sites where risks are greater, a selected range of information may need to be submitted on at least a quarterly basis (e.g. leachate levels, water quality data related to discharges, or data for locations close to or in breach of assessment criteria). Where immediate changes to monitoring schedules are proposed, these should be reported in compliance reports.

For sites which fail to issue notification or compliance reports as required, enforcement action may be taken by SEPA. Enforcement procedures could include either a modification of permit conditions or the serving of a notice requiring information.

### Review reports

A review report should be prepared at least annually and be submitted within three months of the end of the monitoring year. The report should include tabular and graphical presentation of indicator monitoring measurements, including all those used for assessment criteria. The main purpose of this report is to inform site management and SEPA of the environmental performance of the landfill site as well as the performance of the monitoring programme. Recommendations for improving the monitoring system should be made and discussed with SEPA.

Data provided to SEPA with these reports should include all monitoring data collected since the last submission of a review report. All data should be collated into tabular formats. Computerised data records, where available, should be provided electronically in a format agreed with SEPA.

### Update of site control and monitoring plan and risk-based monitoring assessment

The periodic (annual) review includes an assessment not only of the performance of the landfill, but of the performance of the monitoring programme itself. This should allow informed recommendations to be made for updating detail in the site monitoring plan or the risk-based monitoring assessment.

Updating of the risk-based monitoring assessment should be a relatively rare occurrence, normally in response to the re-evaluation of risks following a breach in assessment criteria. Where this is updated, it should be completed prior to updating the site monitoring plan.

Interim changes to the risk-based monitoring assessment or changes required to monitoring infrastructure or monitoring programmes may be made at any time (For example, following breach of an assessment criterion, or damage to a monitoring point). These changes, and any other changes proposed in the annual review report, should be formalised by production of an updated site monitoring plan within six months of the end of the monitoring year.

**Updating the risk-based monitoring assessment**

Examples of situations requiring the risk-based monitoring assessment to be updated include:

* Leachate level or quality that is different to design values.
* Evidence of leachate leakage above design rates.
* Evidence of previously unknown leachate migration pathways and
* New source-pathway-receptor linkage identified (e.g. due to a new abstraction borehole being installed, or land redevelopment).

**Updating the site monitoring plan**

Examples of situations which require the site monitoring plan to be updated include:

* Any alteration to the risk-based monitoring assessment and
* Inability to obtain an appropriate sample from a monitoring point (For example, due to blockage or contamination).

Elements of the site monitoring plan, which are most likely to be subject to periodic revision, include:

* The register of monitoring points (Section 8.3.4).
* The monitoring point location plan (Section 8.3.4).
* Monitoring schedules (Chapter 6).
* Specifications for assessment and compliance criteria (Section 7.2) and
* Statistical baseline data summaries.

Other sections of the site monitoring plan may require less frequent revision. To facilitate updates, the use of a loose-leaf format with dated pages is to be encouraged.

# Selected Bibliography

## Glossary

Nielsen, D.M. (1991). *Practical handbook of ground-water monitoring*. Lewis Publishers Inc. USA ISBN: 087371-124-6.

Porteus, A. (1993). *Dictionary of environmental science and technology*. John Wiley and Sons. UK ISBN: 0471-93544-1.

Whitten, D.G.A. and Brooks, J.R.V. (1978). *The Penguin dictionary of Geology*. Penguin Books. UK ISBN: 0 14 051.0494.

## Chapter 1: Introduction

Blakey, N.C., Young, C.P., Clark, L., and Lewin, K. (1993). *A UK strategy for landfill monitoring*. In: Sardinia 93, Fourth Landfill Symposium, Oct 1993, Cagliari, Italy. 21-47.

Blakey, N.C., Young, C.P., Lewin, K., Clark, L., Turrell, J., and Sims, P. (1997). *Guidelines for monitoring leachate and groundwaters at landfill sites*. Environment Agency. Bristol. Report No. CWM 062/97C.

Clark, L. (1992). *Methodology for monitoring and sampling groundwater*. National Rivers Authority. Bristol. (R & D Note 126).

Commission of the European Communities (1976). *Pollution caused by certain dangerous substances discharged into the aquatic environment of the Community (76/464/EEC)*. Official Journal of the European Communities, L129, 18 May 1976, 23-28.

-------- (1980). *Protection of groundwater against pollution caused by certain dangerous substances (80/68/EEC)*. Official Journal of the European Communities, L20, 26 January 1980, 43-48.

-------- (1998). *Amended proposal for a Council Directive establishing a framework for Community action in the field of water policy (9710/98)*. Interinstitutional File, No 97/0067 (SYN), 19 June 1998, 1-80.

-------- (1998). *Common position for a Council Directive on the landfill of waste*. Official Journal of the European Communities, C333, 30 October 1998, 02, 15-37.

Environment Agency (1996). *LandSim: Landfill performance simulation by Monte Carlo method*. Environment Agency. Bristol. Report No. CWM 094/96

Environmental Data Services (ENDS) (1992). *Dangerous substances in water, a practical guide*. ENDS. London ISBN: 0-907673-05-8.

International Standards Organisation *ISO 5667- 18 : Guidance on sampling groundwaters from potentially contaminated sites*. British Standards Institution. London. (Publication anticipated for Autumn 2000).

-------- (1980). *ISO 5667- 1 : Water quality - sampling - Part 1: Guidance on the design of sampling programmes*. British Standards Institution. London.

-------- (1985). *ISO 5667- 3 : Water quality - sampling - Part 3: Guidance on the preservation and handling of samples*. British Standards Institution. London.

-------- (1987). *ISO 5667- 4 : Water quality - sampling - Part 4: Guidance on sampling from lakes, natural and manmade*. British Standards Institution. London.

-------- (1990). *ISO 5667- 6 : Water quality - sampling - Part 6: Guidance on sampling of rivers and streams*. British Standards Institution. London.

-------- (1991). *ISO 5667- 2 : Water quality - sampling - Part 2: Guidance on sampling techniques*. British Standards Institution. London.

-------- (1991). *ISO 5667- 5 : Water quality - sampling - Part 5: Guidance on sampling of drinking water*. British Standards Institution. London.

-------- (1993). *ISO 5667-11 : Water quality - sampling - Part 11: Guidance on sampling groundwaters*. British Standards Institution. London.

-------- (1995). *ISO 5667- 12 : Water quality - sampling - Part 12: Guidance on sampling of bottom sediments*. British Standards Institution. London.

-------- (1999). *ISO 5667-14 : Water quality - sampling - Part 14: Guidance on quality assurance of environmental sampling and handling*. British Standards Institution. London.

Knox, K. (1991). *A review of water balance methods and their application to landfill in the UK*. Environment Agency. Report No. CWM 031/91.

Lewin, K., Young, C.P., Sims, P., Blakey, N.C., Oakes, D.B., Reynolds, K., and Bradshaw, K. (1996). *Long term monitoring of non-contained landfills: Burntstump and Gorsethorpe on the Sherwood Sandstone*. Environment Agency. Report No. CWM 138/96.

Robinson, H.D. (1995). A *review of the composition of leachates from domestic wastes in landfill sites*. Environment Agency. Report No. CWM/072/95.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

## Chapter 2: Landfills, Leachate and its Effect on Surrounding Waters

Aspinwall & Company (1995). *Review of the behaviour of fluids in landfill sites*. Energy Technology Support Unit (ETSU). Didcot. Report No. B/LF/00465.

Bagchi, A. (1994). *Design, construction and monitoring of landfills*. John Wiley & Sons Inc. USA ISBN: 0471-30681-9.

Barlow, R.J. (1989). *A guide to the use of statistical methods in the physical sciences*. John Wiley & Sons Inc. USA ISBN: 0-471-92294-3.

Beaven, R.P. (1996). *Evaluation of geotechnical and hydrogeological properties of wastes*. In: Engineering geology of waste disposal, Geological Society Engineering Geology Special Publication. No 11, 6-9 September 1993, Cardiff. edited by Bentley, S.P., 57-65. The Geological Society. London.

Blakey, N.C. and Towler, P.A. (1988). *The effect of unsaturated / saturated zone property upon the hydrogeochemical and microbiological processes involved in the migration and attenuation of landfill leachate components*. Water Science Technology, 20, 3, 119-128.

Brassington, R. (1988). *Field hydrogeology*. Geological Society of London professional handbook. Open University Press. Milton Keynes ISBN: 0-335-15202-3.

Christensen, T.H., Bjerg, P.L., Heron, G., Williams, G.M., Higgo, J.J.W., Bourg, A.C.M., and Altmann, R.S. (1994). *Factors controlling the migration and attenuation of priority pollutants in landfill pollution plumes*. Commission of the European Communities. Report No. CT90069.

Christensen, T.H., Bjerg, P.L., and Kjeldsen, P. (2000). *Natural attenuation: a feasible approach to remediation of ground water pollution at landfills?* Ground Water Monitoring Review, Winter 2000, 69-77.

Christensen, T.H., Kjeldsen, P., Albrechtsen, H.J., Heron, G., Nielsen, P.H., Bjerg, P.L., and Holm, P.E. (1994). *Attenuation of landfill leachate pollutants in aquifers*. Critical Reviews in Environmental Science and Technology, 24, 2, 119-202.

Croft, B. and Campbell, D.J.V. (1990). *Characterisation of 100 UK landfills*. In: Proceedings Harwell Waste Management Symposium, AEA Environment and Energy, Harwell, Oxon. 130-29.

-------- (1992). *Characterisation of one hundred United Kingdom landfill sites*. Environment Agency. Report No. CWM 015/90.

Department of the Environment (DoE) (1979). *Co-operative programme of research on the behaviour of hazardous wastes in landfill sites ("The brown book")*. HMSO. London.

-------- (1999). *Methodology for the derivation of remedial targets for soil and groundwater to protect water resources*. Environment Agency. Report No. R&D Publication 20.

Erskine, A.D. (2000). *Transport of ammonium in aquifers: retardation and degradation*. Quarterly Journal of Engineering Geology, 33, 161-170.

Fleet, M. and Lewin, K. (1993). *Monitoring for leachate migration from landfills in Magnesian limestone quarries at Old Wingate and Joint Stocks, Durham: 1984-1992*. Environment Agency. Report No. CWM 060/93.

Fleet, M., Young, C.P., Blakey, N.C., and Lewin, K. (1994). *Landfill site monitoring investigations at the Ingham landfill sites: 1974-92. Final Report*. Environment Agency. Report No. CWM 052/94.

Gray, D.A., Mather, J.D., and Harrison, I.B. (1974). *Review of groundwater pollution from waste disposal sites in England and Wales with provisional guidelines for future site selection*. Quarterly Journal of Engineering Geology, 7, 181-196.

Hammerton, D. (1997). *An introduction to water quality in rivers coastal waters and estuaries*. CIWEM Booklet 5. Chartered Institute of Wastes and Environmental Management. London ISBN: 1-870752-27-\*9.

Harris, R.C. (1988). *Leachate migration in the unsaturated zone of the Triassic Sandstones*. In: Gronow, J.R., Schofield, A. N., and Jain, R. K., Ed. Land disposal of hazardous waste engineering and environmental issues. Ellis Horwood, Chichester. pp. 175-186.

Harris, R.C. and Parry, E.L. (1982). *Investigations into domestic refuse leachate attenuation in the unsaturated zone of Triassic sandstones*. In: Effects of waste disposal on groundwater and surface water, IAHS Publ. No. 139, Jul 1982, Exeter Symposium. 147-155.

IWM Sustainable Landfill Working Group (1999). *The role and operation of the flushing bioreactor*. Institute of Wastes Management. Northampton.

Keating, T. and Packman, M.J. (1995). *Guide to groundwater protection zones in England & Wales*. National Rivers Authority/ HMSO. London ISBN: 0-11-310104-X.

Knox, K. (1991). *A review of water balance methods and their application to landfill in the UK*. Environment Agency. Report No. CWM 031/91.

-------- (1996). *Leachate recirculation in its role in sustainable development*. Institute of Waste Management Proceedings, March 1996, 10-15. IWM Northampton.

Knox, K. and de Rome, L. (1998). *Practical benefits for the waste management industry from the UK's landfill cell test programme*. Wastes Management, November, 18-19.

Kunkle, G.R. and Shade, J.W. (1975). *Monitoring ground-water quality near a sanitary landfill*. Ground Water, 14, 1.

Lerner, D.N. and Walton, N.R.G. (1998). *Contaminated land and groundwater: future directions*. Geological Society Special Publication No 14. Geological Society. ISBN: 1-86239-001.

Lewin, K., Young, C.P., Bradshaw, K., Fleet, M., and Blakey, N.C. (1994). *Landfill monitoring investigations at Burntstump landfill*. Sherwood Sandstone, Nottingham 1978-93. Environment Agency. Report No. CWM 035/94.

Lloyd, J.W., Greswell, R., Williams, G.M., Ward, R.S., Mackay, R., and Riley, M.S. (1996). *An integrated study of controls on solute transport in the Lincolnshire Limestone*. Quarterly Journal of Engineering Geology, 29, 321-340.

Mather, J.D. (1977). *Attenuation and control of landfill leachates*. In: Institute of solid wastes management 79th annual conference, 31 May - 3 June 1977, Torbay. IWM. Northampton.

-------- (1989). The *attenuation of the organic component of landfill leachate in the unsaturated zone: a review*. Quarterly Journal of Engineering Geology, 22, 241-246.

Mather, J.D., Banks, D., Dumpleton, S., and Fermor, M. (1997). *Groundwater contaminants and their migration*. Geological Society Special Publication No 128. Geological Society. ISBN: 1-897799-95-0.

North West Waste Disposal Officers (1991). *Leachate Management Report.* Lancashire Waste Disposal Authority. Leyland, Lancashire.

Osborn, D., Malcolm H.M, Wright, J., Freestone, P., Wyatt, C., and French, M.C. (1994). *Assessment of the role of landfill operations in the contamination of wildlife by organic and inorganic substances*. Environment Agency: National Groundwater and Contaminated Land Centre. Report No. CWM 102/94.

Powrie, W. and Beaven, R.P. (1998). *Hydraulic conductivity of waste: current research and implications for leachate management*. Wastes Management, November, 22-23.

Price, M. (1996). *Introducing groundwater*. Chapman Hall. UK ISBN: 04 12485001.

Purcell, B.E., Butler, A.P., Sollars, C.J., and Buss, S.E. (1999). *Leachate ammonia flushing from landfill simulators*. Journal of Chartered Institution of Water and Environmental Management, 13, 107-111.

Robins, N.S. (1998). *Groundwater pollution, aquifer recharge and vulnerability*. Geological Society Special Publication No 130. Geological Society. ISBN: 1-897799-98-5.

Robinson, H.D. and Gronow, J.R. (1995). *A review of landfill leachate composition in the UK*. Institute of Waste Management Proceedings, January 1995, 3-8. IWM. Northampton.

-------- (1996). *Tritium levels in leachates and condensates from domestic wastes in landfill sites*. Journal of Chartered Institution of Water and Environmental Management, 10, 6, 391-398.

Thornton, S.F., Lerner, D.N., and Tellam, J.H. (1995). Lab*oratory studies of landfill leachate - Triassic Sandstone interactions*. Environment Agency. Report No. CWM 035A/94.

Thornton, S.F., Tellam, J.H., and Lerner, D.N. (1997). *Experimental and modelling approaches for the assessment of chemical impacts of leachate migration from landfills: A case study of a site on the Triassic Sandstone aquifer in the UK East Midlands*. In: Geo-engineering of hazardous and radioactive waste disposal, 10-14 September, 1997, Newcastle-upon-Tyne.

US Environmental Protection Agency (1990). *Handbook. Ground water. Volume 1: Ground water and contamination*. EPA. USA. Ref: EPA/625/6-90/016a.

West, G. (1991). *The field description of engineering soils and rocks*. Geological Society of London professional handbook. Open University Press. Buckingham ISBN: 0-335-15208-2.

Westlake, K., Sayce, M., and Fawcett, T. (1991). *Environmental impacts from landfills accepting non-domestic wastes*. Environment Agency. Report No. CWM 036/91.

World Health Organisation (WHO) (1985). *Guidelines for drinking-water quality. Vol 1: recommendations*. HMSO. London ISBN: 92-4-154168-7.

-------- (1985). *Guidelines for drinking-water quality. Vol 2: health criteria and other supporting information*. HMSO. London ISBN: 92-4-154169-5.

-------- (1985). *Guidelines for drinking-water quality. Vol 3: drinking-water quality control in small-community supplies*. HMSO. London ISBN: 92-4-154170-9.

Young, C.P., Fleet, M., Lewin, K., Blakey, N.C., and Bradshaw, K. (1994). *Landfill site monitoring investigations at Gorsethorpe landfill*. Sherwood Sandstone, Nottinghamshire 1978-92. Environment Agency. Report No. CWM 034/94.

Younger, P.L. and Elliot, T. (1995). *Chalk fracture system characteristics: implications for flow and solute transport*. Quarterly Journal of Engineering Geology, 28, S39-S50.

## Chapter 3: Monitoring Principles

Blakey, N.C., Young, C.P., Lewin, K., Clark, L., Turrell, J., and Sims, P. (1997). *Guidelines for monitoring leachate and groundwaters at landfill sites*. Environment Agency. Bristol. Report No. CWM 062/97C.

Carson, P.A. and Dene, N.J. (1990). *Good laboratory practices. Techniques for the quality assurance professional*. Butterworth - Heinemann. UK

Cheeseman, R.V. and Wilson, A.L. (1989). revised by Gardner, June 1989. *A manual on analytical quality control for the water industry*. Water Research Centre plc. Report No. NS30.

Commission of the European Communities (1980). *Protection of groundwater against pollution caused by certain dangerous substances (80/68/EEC)*. Official Journal of the European Communities, L20, 26 January 1980, 43-48.

Gibbons, R.D. (1994). *Statistical methods for groundwater monitoring*. John Wiley & Sons Inc. USA ISBN: 158707-9.

-------- (1999). *Use of combined Shewart-CUSUM control charts for ground water monitoring applications*. Ground Water, 37, 5, 682-691.

Gibbons, R.D., Dolan, D.G., May, H., O'Leary, K., and O'Hara, R. (1999). *Statistical comparison of leachate from hazardous, codisposal and municipal solid waste landfills*. Ground Water Monitoring Review, Fall 1999, 57-72.

Health and Safety Executive (1989). *Quantified risk assessment: Its input to decision making*. UK ISBN: 0 11 8854992.

Knox, K., Robinson, H.D., van Santen, A., and Tempany, P.R. (2000). *The occurrence of trace organic components in landfill leachates and their removal during on-site treatment*. IWM Scientific & Technical Review, November, 5-10. IWM Business Services Ltd. Northampton.

Lee, G.F. and Jones, R.A. (1992). *A closer look at what’s needed for reliable monitoring of lined landfills*. Solid Waste and Power, 48-52.

Oakland, J.S. (1996). *Statistical process control - a really practical guide*. Butterworth - Heinemann. UK

Perry, D. and Thompson, J. (1998). *Collecting and analysing data for waste sampling and monitoring*. Institute of Waste Management Proceedings, March, 4-7. IWM. Northampton.

Ramsey, M.H. (1998). *Switching from representative to appropriate sampling, and from deterministic to probabilistic interpretations*. Institute of Waste Management Proceedings, March, 16-20. IWM. Northampton.

Sheils, A.K. (1993). *Hydrogeology and European Legislation*. Quarterly Journal of Engineering Geology, 26, 227-232.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

Thompson, M. (1995). *Uncertainty in an uncertain world*. Analyst, 120, 117-118.

## Chapter 4: Risk-Based Monitoring

Department of the Environment (DoE) (1994). *A framework for assessing the impact of contaminated land on groundwater and surface water*. Vol 1 & 2. HMSO.

Department of the Environment, T.a.R.D. (2000). *Guidelines for environmental risk assessment and management*. TSO. London.

Environment Agency (1996). *LandSim: Landfill performance simulation by Monte Carlo method*. Environment Agency. Bristol. Report No. CWM 094/96.

-------- (1999). *Methodology for the derivation of remedial targets for soil and groundwater to protect water resources*. Environment Agency. Report No. R&D Publication 20.

Erskine, A.D. (2000). *Transport of ammonium in aquifers: retardation and degradation*. Quarterly Journal of Engineering Geology, 33, 161-170.

Health and Safety Executive (1989). *Quantified risk assessment: Its input to decision making*. UK ISBN: 0 11 8854992.

## Chapter 5: Design Issues and Monitoring Objectives

International Standards Organisation (1980). *ISO 5667- 1 : Water quality - sampling - Part 1: Guidance on the design of sampling programmes*. British Standards Institution. London.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

Waste Management Industry Training and Advisory Board (WAMITAB) (1998). *Preparation for assessment: Managing landfill operations, biodegradable waste*. WAMITAB. London. (Workbook Section L4B-8.2).

## Chapter 6: Monitoring Locations and Schedules

Clark, L. (1992). *Methodology for monitoring and sampling groundwater*. National Rivers Authority. Bristol. (R & D Note 126).

Environmental Data Services (ENDS) (1992). *Dangerous substances in water, a practical guide*. ENDS. London ISBN: 0-907673-05-8.

Hammerton, D. (1997). *An introduction to water quality in rivers coastal waters and estuaries*. CIWEM Booklet 5. Chartered Institute of Wastes and Environmental Management. London ISBN: 1-870752-27-\*9.

Keith, L.H. (1996). *Environmental sampling and analysis: a practical guide*. Lewis Publishers Inc. USA ISBN: 0-87371-381-8.

Nativ, R., Adar, E.M., and Becker, A. (1999). *Designing a monitoring network for contaminated ground water in fractured chalk*. Ground Water, 37, 1, 38-46.

Nielsen, D.M. (1991). *Practical handbook of ground-water monitoring*. Lewis Publishers Inc. USA ISBN: 087371-124-6.

Price, M. (1996). *Introducing groundwater*. Chapman Hall. UK ISBN: 04 12485001.

Robinson, H.D. and Gronow, J.R. (1995). *A review of landfill leachate composition in the UK*. Institute of Waste Management Proceedings, January 1995, 3-8. IWM. Northampton.

-------- (1996). *Tritium levels in leachates and condensates from domestic wastes in landfill sites*. Journal of Chartered Institution of Water and Environmental Management, 10, 6, 391-398.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

## Chapter 7: Assessment Criteria and Contingency Planning

Commission of the European Communities (1998). *Common position for a Council Directive on the landfill of waste*. Official Journal of the European Communities, C333, 30 October 1998, 02, 15-37.

Gibbons, R.D. (1994). *Statistical methods for groundwater monitoring*. John Wiley & Sons Inc. USA ISBN: 158707-9.

-------- (1999). *Use of combined Shewart-CUSUM control charts for ground water monitoring applications*. Ground Water, 37, 5, 682-691.

Keith, L.H. (1996). *Environmental sampling and analysis: a practical guide*. Lewis Publishers Inc. USA ISBN: 0-87371-381-8.

Kendall, M. and Ord, J.K. (1993). *Time series*. Arnold. UK

Montgomery, D.C. (1991). *Introduction to statistical quality control*. John Wiley and Sons Inc. USA

Oakland, J.S. (1996). *Statistical process control - a really practical guide*. Butterworth - Heinemann. UK

Smith, A.C. and Gee, D.R. (1983). *The development and application of a pollution index as an aid to management of waste disposal sites*. Journal of The Association of Public Analysts, 21, 135-140.

Thompson, J. and Perry, D. (1998). *Landfill monitoring, data handling and analysis in the context of current and future guidance and legislation*. Institute of Waste Management Proceedings, December, 13-16. IWM. Northampton.

## Chapter 8: Design of Monitoring Points

Aller, L., Bennett, T.W., Hackett, G., Petty, R.J., Lehr, J.H., Sedoris, H., Nielsen, D.M., and Denne, J.E. (1989). H*andbook of suggested practices for the design and installation of ground-water monitoring wells*. National Water Well Association. USA. Ref: EPA 600/4-89/034 1989.

Association of Geotechnical Specialists (1992). *Safety manual for investigation sites*. PO Box 250, Camberley, UK.

Bishop, P.K., Burston, M.W., Chen, T., and Lerner, D.N. (1991). *A low cost dedicated multi-level groundwater sampling system*. Quarterly Journal of Engineering Geology, 24, 311-321.

Brandon, T.W. (1986). *Groundwater occurrence, development and protection*. Water Practices Manuals. 5. Institution of Water Engineers and Scientists. ISBN: 0-901427-14-4.

British Drilling Association (1981). *Code of safe drilling practice. (Part 1: Surface drilling)*. Brentwood, Essex.

British Standards Institution (1983). *British Standard BS6316: Code of practice for test pumping of water wells*. London.

-------- (1999). *British Standard BS5930: Code of practice for site investigations*. London.

Cherry, J.A. and Johnson, P.E. (1982). *A multilevel device for monitoring in fractured rock*. Ground Water Monitoring Review, Summer, 41-44.

Clark, L. (1988). *The field guide to water wells and boreholes*. Geological Society of London Professional Handbook. Open University Press. Milton Keynes ISBN: 0-335-15203-1.

Clark, L. and Baxter, K.M. (1989). *Groundwater sampling techniques for organic micropollutants: UK experience*. Quarterly Journal of Engineering Geology, 22, 159-168.

Cox, S. and Powrie, W. (2000). *Horizontal wells for leachate control in landfills*. Wastes Management, December, 35-37.

Driscol, F.G. (1986). *Groundwater and wells*. St Paul, Minnesota, Johnson Division. USA

Dumble, J.P., Charlesworth, D.L., and Haynes, J. (1993). *Groundwater monitoring protocols around landfill sites: The influence of well design, purging methods and sediment on the integrity of groundwater samples*. In: Discharge Your Obligations, 2-4 November 1993, Kenilworth, Warwickshire. edited by Hall, K.E. and Coombs, J., 175-184. CPL Press. Newbury.

Dutta, D., Das Gupta, A., and Ramnarong, V. (1998). *Design and optimisation of a ground water monitoring system using GIS and multicriteria decision analysis*. Ground Water Monitoring Review, 18, 1, 139147.

Hubbell, J.M., Wood, T.R., Higgs, B., Wylie, A.H., and McElroy, D.L. (1998). *Design, installation, and uses of combination ground water and gas sampling wells*. Ground Water Monitoring Review, 18, 3, 151157.

Hudak, P.F. (1998). *Configuring detection wells near landfills*. Ground Water Monitoring Review, 18, 2, 9396.

International Standards Organisation (1993). *ISO 5667-11 : Water quality - sampling - Part 11: Guidance on sampling groundwaters*. British Standards Institution. London.

IWM Landfill Gas Monitoring Working Group (1998). *The monitoring of landfill gas*. Institute of Wastes Management. Northampton.

Jardine, K., Smith, L., and Clemo, T. (1996). *Monitoring networks in fractured rocks: a decision analysis approach*. Ground Water, 34, 3, 504-518.

Johnson, T.L. (1983). *A comparison of well nests vs. single-well completions*. Ground Water Monitoring Review, 3, 1, 76-78.

Jones, I. and Lerner, D.N. (1995). *Level-determined sampling in an uncased borehole*. Journal of Hydrology, 171, (Special issue on groundwater sampling), 291-317.

-------- (1997). *Multilevel groundwater sampling: towards a cost effective solution*. Geo-engineering of hazardous and radioactive waste disposal, 1 Sep 1997-14 Sep 1997, Newcastle upon Tyne. 223-236. Geological Society

Jones, I., Lerner, D.N., and Baines, O.P. (1999). *Multiport socks samplers: a low cost technology for effective multilevel ground water sampling*. Ground Water Monitoring and Remediation, Winter, 134-142.

Lerner, D.N. and Jones, I. (1995). *Multilevel sampling in open boreholes: problems and a new solution*. IAH Congress Solutions ‘95, Edmonton, Canada.

Lerner, D.N. and Teutsch, G. (1995). *Recommendations for level-determined sampling in wells*. Journal of Hydrology, 171, (Special issue on groundwater sampling)., 255-377.

Patton, F.D. and Smith, H.R. (1988). *Design considerations and the quality of data from multiple level groundwater monitoring wells*. in: Collins, A.G. and Johnson, A. I., Editors. Ground-Water contamination:

Field methods, ASTM STP 963. Philadelphia, USA. American Society for Testing and Materials. pp. 206-217.

Pianosi, J.G. and Weaver, T.R. (1991). *Multilevel groundwater assessment of confining units in a bedrock sequence near Sarnia, Ontario*. in: American Institute of Hydrology. Hydrology and Hydrogeology in the'90s. pp. 126-134.

Schirmer, M., Jones, I., Teutsch, G., and Lerner, D.N. (1995). *Development and testing of multiport sock samplers for groundwater*. Journal of Hydrology, 171, (Special issue on groundwater sampling), 239257.

Site Investigation Steering Group (1993). *Guidelines for the safe investigation by drilling of landfills and contaminated land. Site investigation in construction series. Volume 4*. Thomas Telford Services Ltd. London.

-------- (1993). *Planning, procurement and quality management. Site investigation in construction series. Volume 2*. Thomas Telford Services Ltd. London.

-------- (1993). *Specification for ground investigations. Site investigation in construction series. Volume 3*. Thomas Telford Services Ltd. London.

-------- (1993). *Without site investigation ground is a hazard. Site investigation in construction series. Volume 1*. Thomas Telford Services Ltd. London.

Smith, H.R. and et al (1984). *Modular piezometer system*. Geotechnical News, 2, 4, 44-46.

US Army Corps of Engineers (1994). *Monitor well design, installation, and documentation at hazardous and/or toxic waste sites*. USA. Ref: Manual 1110-1-4000.

## Chapter 9: Monitoring Methodology

American Society for Testing and Materials (1992). *ASTM Standard D4696-92: Pore-liquid sampling from the vadose zone*.

-------- (1997). *ASTM Standards on environmental sampling*. ASTM. USA. Ref: 03-418097-38. ISBN: 0-80311835-X.

Backhus, D.A., Ryan, J.N., Groher, D.M., MacFarlane, J.K., and Gschwend, P.M. (1993). *Sampling colloids and colloid-associated contaminants in ground water*. Ground Water, 31, 3, 466-479.

Barber, C. and Davis, G.B. (1987). *Representative sampling of ground water from short-screened boreholes*. Ground Water, 25, 5, 581-587.

Barcelona, M.J. and Gibb, J.P. (1988). *Development of effective groundwater sampling protocols*. In: Groundwater contamination: field methods, edited by Collins, A.G. and Johnson, A.I., 17-26. ASTM. USA.

Barcelona, M.J. and Helfrich, J.A. (1986). *Well construction and purging effects on groundwater samples*. Environmental Science and Technology, 20, 11, 1179-1184.

Barcelona, M.J., Helfrich, J.A., and Garske, E.E. (1988). *Verification of sampling methods and selection of materials for groundwater contamination*. In: Groundwater contamination: field methods, edited by Collins, A.G. and Johnson, A.I., 221-231. ASTM. USA.

Barcelona, M.J., Helfrich, J.A., Garske, E.E., and Gibb, J.P. (1984). *A laboratory evaluation of groundwater sampling mechanisms*. Ground Water Monitoring Review, 4, 2, 32-41.

Barker, J.F. and Dickhout, R. (1988). *An evaluation of some systems for sampling gas-charged ground water for volatile organic analysis*. Ground Water Monitoring Review, 8, 4, 112-120.

Barker, J.F., Patrick, G.C., Lemon, L., and Travis, G.M. (1987). *Some biases in sampling multilevel piezometers for volatile organics*. Ground Water Monitoring Review, 7, 2, 48-54.

Blakey, N.C., Bradshaw, K., and Lewin, K. (1998). *Leachate monitoring for the Brogborough test cell project*. Environment Agency. Report No. EPG 1/7/13.

Blakey, N.C., Young, C.P., Clark, L., and Lewin, K. (1993). *A UK strategy for landfill monitoring*. In: Sardinia 93, Fourth Landfill Symposium, Oct 1993, Cagliari, Italy. 21-47.

British Standards Institution (1993). *British Standard BS6068 (Water Quality), Section 6.11: Guidance on sampling of groundwaters*. London.

Charlesworth, D.L., Howard, K.W.F., and Nadon, R.L. (1992). *An innovative use of groundwater sampling equipment to determine aquifer characteristics in Precambrian basement rocks of Uganda*. Quarterly Journal of Engineering Geology, 25, 165-168.

Cheeseman, R.V. and Wilson, A.L. (1989). revised by Gardner, June 1989. *A manual on analytical quality control for the water industry*. Water Research Centre plc. Report No. NS30.

Church, P.E. and Granato, G.E. (1996). *Bias in groundwater data caused by well-bore flow in lon-screen wells*. Ground Water, 34, 2, 262-273.

Department of the Environment (DoE) (1989). *Guidance on safeguarding the quality of public water supplies*. HMSO. London.

Dumble, J.P., Charlesworth, D.L., and Haynes, J. (1993). *Groundwater monitoring protocols around landfill sites: The influence of well design, purging methods and sediment on the integrity of groundwater samples*. In: Discharge Your Obligations, 2-4 November 1993, Kenilworth, Warwickshire. edited by Hall, K.E. and Coombs, J., 175-184. CPL Press. Newbury.

Environmental Data Services (ENDS) (1992). *Dangerous substances in water, a practical guide*. ENDS. London ISBN: 0-907673-05-8.

Gale, I.N. and Robins, N.S. (1989). *The sampling and monitoring of groundwater quality*. Hydrogeology Series. Department of the Environment. Report No. WD/89/7.

Gibs, J., Brown, G., Turner, K.S., Macleod, C.L., Jelinski, J.C., and Koehnlein, S.A. (1993). *Effects of smallscale vertical variations in well-screen inflow rates and concentrations of organic compounds on the collection of representative ground-water-quality samples*. Ground Water, 31, 2, 201-208.

Gibs, J. and Imbrigiotta, T.E. (1990). *Well-purging criteria for sampling purgeable organic compounds*. Ground Water, 28, 1, 68-78.

Gibs, J., Szabo, Z., Ivahnenko, T., and Wilde, F.D. (2000). *Change in field turbidity and trace element concentrations during well purging*. Ground Water, 38, 4, 577-588.

Hammerton, D. (1997). *An introduction to water quality in rivers coastal waters and estuaries*. CIWEM Booklet 5. Chartered Institute of Wastes and Environmental Management. London ISBN: 1-870752-27-\*9.

Haynes, J., Henderson, K., and Charlesworth, D.L. (1992). *Landfill monitoring: a comparison of the cost, reliability and convenience of various methods of groundwater sampling*. In: Discharge Your Obligations, 10-12 March 1992, Kenilworth, Warwickshire. edited by Hall, K.E. and Alston Coombs, Y.R., 195-202. CPL Press. Newbury.

Hazelton, C. (1998). *Variations between continuous and spot-sampling techniques in monitoring a change in river-water quality*. Journal of Chartered Institution of Water and Environmental Management, 12, 2, 124-129.

Hitchman, S.P. (1983). *A guide to the field analysis of groundwater*. Fluid Processes Unit. Institute of Geological Sciences. London. Report No. FLPU 83-12.

Howsam, P. and Thakoordin, M. (1996). *Groundwater quality monitoring: the use of flow-through cells*. Journal of Chartered Institution of Water and Environmental Management, 10, 6, 407-410.

Hutchins, S.R. and Acree, S.D. (2000). *Ground water sampling bias observed in shallow conventional wells*. Ground Water Monitoring Review, Winter 2000, 86-93.

International Standards Organisation *ISO 5667- 18 : Guidance on sampling groundwaters from potentially contaminated sites*. British Standards Institution. London. (Publication anticipated for Autumn 2000).

-------- (1980). *ISO 5667- 1 : Water quality - sampling - Part 1: Guidance on the design of sampling programmes*. British Standards Institution. London.

-------- (1985). *ISO 5667- 3 : Water quality - sampling - Part 3: Guidance on the preservation and handling of samples*. British Standards Institution. London.

-------- (1986). *ISO 8363: Liquid flow measurement in open channels: General guidelines for the selection of methods*. British Standards Institution. London.

-------- (1987). *ISO 5667- 4 : Water quality - sampling - Part 4: Guidance on sampling from lakes, natural and man made*. British Standards Institution. London.

-------- (1990). *ISO 5667- 6 : Water quality - sampling - Part 6: Guidance on sampling of rivers and streams*. British Standards Institution. London.

-------- (1991). *ISO 5667- 2 : Water quality - sampling - Part 2: Guidance on sampling techniques*. British Standards Institution. London.

-------- (1991). *ISO 5667- 5 : Water quality - sampling - Part 5: Guidance on sampling of drinking water*. British Standards Institution. London.

-------- (1993). *ISO 5667-11 : Water quality - sampling - Part 11: Guidance on sampling groundwaters*. British Standards Institution. London.

-------- (1995). *ISO 5667- 12 : Water quality - sampling - Part 12: Guidance on sampling of bottom sediments*. British Standards Institution. London.

-------- (1999). *ISO 5667-14 : Water quality - sampling - Part 14: Guidance on quality assurance of environmental sampling and handling*. British Standards Institution. London.

Kearl, P.M., Korte, N.E., and Cronk, T.A. (1992). *Suggested modifications to ground water sampling procedures based on observations from colloidal borescope*. Ground Water Monitoring Review, 12, 2, 155-161.

Kearl, P.M., Korte, N.E., Stites, M., and Baker, J. (1994). *Field comparison of micropurging vs. traditional ground water sampling*. Ground Water Monitoring Review, 14, 4, 183-190.

Keely, J.F. (1982). *Chemical time series sampling*. Ground Water Monitoring Review, 2, 4, 29-38.

Keely, J.F. and Boateng, K. (1987). *Monitoring well installation, purging, and sampling techniques - part 2: case histories*. Ground Water, 25, 4, 427-439.

Keith, L.H. (1996). *Environmental sampling and analysis: a practical guide*. Lewis Publishers Inc. USA ISBN: 0-87371-381-8.

Knox, K. (1991). *A review of water balance methods and their application to landfill in the UK*. Environment Agency. Report No. CWM 031/91.

Martin-Hayden, J.M. (2000). *Controlled laboratory investigations of wellbore concentration response to pumping*. Ground Water, 38, 1, 121-128.

-------- (2000). *Sample concentration response to laminar wellbore flow: implications to ground water data variability*. Ground Water, 38, 1, 12-19.

Mickam, J.T., Bellandi, R., and Tifft, E.C.Jr. (1989). *Equipment decontamination procedures for ground water and vadose zone monitoring programs: status and prospects*. Ground Water Monitoring Review, 9, 2, 100-121.

Nielsen, D.M. (1991). *Practical handbook of ground-water monitoring*. Lewis Publishers Inc. USA ISBN: 087371-124-6.

Sukop, M.C. (2000). *Estimation of vertical concentration profiles from existing wells*. Ground Water, 38, 6, 836-841.

Parker, L.V., Hewitt, A.D., and Jenkins, T.F. (1990). *Influence of casing materials on trace-level chemicals in well water*. Ground Water Monitoring Review, 10, 2, 146-156.

Parker, L.V. and Ranney, T.A. (1997). *Sampling trace-level organic solutes with polymeric tubing. Part 1. Static studies*. Ground Water Monitoring Review, 17, 4, 115-124.

-------- (1998). *Sampling trace-level organic solutes with polymeric tubing. Part 2. Dynamic studies*. Ground Water Monitoring Review, 18, 1, 148-155.

-------- (2000). *Decontaminating materials used in ground water sampling devices: organic contaminants*. Ground Water Monitoring Review, Winter 2000, 56-68.

Price, M. and Williams, A. (1993). *The influence of unlined boreholes on groundwater chemistry: a comparative study using pore-water extraction and packer sampling*. Journal of Institution of Water and Environmental Management, 7, 6, 650-659.

Puls, R.W. and Powell, R.M. (1992). *Acquisition of representative ground water quality samples for metals*. Ground Water Monitoring Review, 12, 3, 167-176.

Ramsey, M.H. (1998). *Switching from representative to appropriate sampling, and from deterministic to probabilistic interpretations*. Institute of Waste Management Proceedings, March, 16-20. IWM. Northampton.

Ranney, T.A. and Parker, L.V. (1998). *Comparison of fiberglass and other polymeric well casings. Part 3. Sorption and leaching of trace-level metals*. Ground Water Monitoring Review, 18, 3, 127-133.

Rannie, E.H. and Nadon, R.L. (1988). *An inexpensive, multi-use, dedicated pump for ground water monitoring wells*. Ground Water Monitoring Review, 8, 4, 100-107.

Reilly, T.E. and LeBlanc, D.R. (1998). *Experimental evaluation of factors affecting temporal variability of water samples obtained from long-screened wells*. Ground Water, 36, 4, 556-576.

Reynolds, G.W., Hoff, J.T., and Gillham, R.W. (1990). *Sampling bias caused by materials used to monitor halocarbons in groundwater*. Environmental Science and Technology, 24, 1, 135-142.

Robin, M.J.L. and Gillham, R.W. (1987). *Field evaluation of well purging procedures*. Ground Water Monitoring Review, 7, 4, 85-93.

Saar, R.A. (1997). *Filtration of ground water samples: a review of industry practice*. Ground Water Monitoring Review, 17, 1, 56-62.

Schalla, R., Myers, D.A., Simmons, M.A., Thomas, J.M., and Toste, A.P. (1988). *The sensitivity of four monitoring well sampling systems to low concentrations of three volatile organics*. Ground Water Monitoring Review, 18, 3, 90-96.

Sevee, J., White, C.A., and Maher, D.J. (2000). *An analysis of low-flow ground water sampling methodology*. Ground Water Monitoring Review, Spring 2000, 87-93.

Shanklin, D.E., Sidle, W.C., and Ferguson, M.E. (1985). *Micro-purge low-flow sampling of uranium contaminated ground water at the Fernald environmental management project*. Ground Water Monitoring Review, 5, 3, 168-176.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

Stuart, A. (1984). *Borehole sampling techniques in groundwater pollution studies*. Fluid Processes Unit. Institute of Geological Sciences. London. Report No. FLPU 84-15.

Stuart, A. and Hitchman, S.P. (1986). *Borehole sampling techniques and field analysis of groundwater in landfill pollution studies*. In: Groundwater in engineering geology, Geological Society Engineering Geology Special Publication. No 3, edited by Cripps, J.C., Bell, F.G., and Culshaw, M.G., 225-246. The Geological Society. London.

US Environmental Protection Agency (1990). *Handbook. Ground water. Volume 1: Ground water and contamination*. EPA. USA. Ref: EPA/625/6-90/016a.

-------- (1991). *Handbook. Ground water. Volume 2: Methodology*. EPA. USA. Ref: EPA/625/6-90/016b.

-------- (1994). *RCRA Ground water monitoring: Draft technical guidance*. Government Institutes, Inc. USA ISBN: 0-86587-376-6.

-------- (1996). *RCRA Ground water monitoring technical enforcement guidance document*. USA

## Chapter 10: Data Management and Reporting

Berthouex, P.M. and Brown, L.C. (1994). *Statistics for environmental engineers*. CRC Press Inc. USA ISBN: 1-56670-031-0.

Gibbons, R.D. (1987). *Statistical models for the analysis of volatile organic compounds in waste disposal sites*. Ground Water, 25, 4, 455-465.

-------- (1987). *Statistical prediction intervals for the evaluation of ground-water quality*. Ground Water, 25, 4, 455-465.

-------- (1994). *Statistical methods for groundwater monitoring*. John Wiley & Sons Inc. USA ISBN: 1-58707-9.

-------- (1999). *Use of combined Shewart-CUSUM control charts for ground water monitoring applications*. Ground Water, 37, 5, 682-691.

Gibbons, R.D., Dolan, D.G., May, H., O'Leary, K., and O'Hara, R. (1999). *Statistical comparison of leachate from hazardous, codisposal and municipal solid waste landfills*. Ground Water Monitoring Review, Fall 1999, 57-72.

Hem, J.D. (1975). *Study and interpretation of the chemical characteristics of natural water*. US Government Printing Office. Washington DC

Kendall, M. and Ord, J.K. (1993). *Time series*. Arnold. UK

Lachance, A.D. and Stoline, M.R. (1995). *The application of a statistical trend analysis model to ground water monitoring data from solid waste landfills*. Ground Water Monitoring Review, 15, 4, 163-174.

Martin-Hayden, J.M. (2000). *Controlled laboratory investigations of wellbore concentration response to pumping*. Ground Water, 38, 1, 121-128.

-------- (2000). *Sample concentration response to laminar wellbore flow: implications to ground water data variability*. Ground Water, 38, 1, 12-19.

Mazor, E. (1991). *Applied chemical and isotopic groundwater hydrology*. Open University Press. Great Britain ISBN: 0-335-15212-0.

Mew, H.E.J., Medina Jr, M.A., Heath, R.C., Reckhow, K.H., and Jacobs, T.L. (1997). *Cost-effective monitoring strategies to estimate mean water table depth*. Ground Water, 35, 6, 1089-1096.

Montgomery, D.C. (1991). *Introduction to statistical quality control*. John Wiley and Sons Inc. USA

Oakes, D.B. (1977). *Use of idealised models in predicting the pollution of water supplies due to leachate from landfill sites*. In: Water Research Centre conference on groundwater quality, measurement, prediction and protection, 1977, WRC Medmenham. 524-611.

Oakland, J.S. (1996). *Statistical process control - a really practical guide*. Butterworth - Heinemann. UK

Ross, L.D. (1997). *Multivariate statistical analysis of environmental monitoring data*. Ground Water, 35, 6, 1050-1957.

Thompson, J. and Perry, D. (1998). *Landfill monitoring, data handling and analysis in the context of current and future guidance and legislation*. Institute of Waste Management Proceedings, December, 13-16. IWM. Northampton.

Tonjes, D.J., Heil, J.H., and Black, J.A. (1995). *Sliding stiff diagrams: a sophisticated ground water analytical tool*. Ground Water Monitoring Review, 15, 2, 134-139.

# Appendix 1: Example Monitoring Point Construction Forms and Registers

## A1.1 Monitoring point construction record sheet for wells and boreholes

An example form for a single monitoring point in a borehole is provided as Table A1.1a which could be used for most groundwater or leachate monitoring points. A continuation form (Table A1.1b) is provided to record details of multiple installations within a single borehole. The forms should be used in association with other records such as borehole logs and could be used as a basis for transferring information to a database.

Descriptions of information and examples applicable to each heading are provided by the following:

**Table A1.1a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Borehole Ref: | Borehole reference number  For boreholes containing a single monitoring point this will usually be the same as the “Mon. Point Ref No”  For boreholes containing multiple installations this will usually be the same as the “Multi Ref” number.  This should be an alphanumeric number which is unique at a particular site (avoid use of the characters: \*, /, \, -, \_, brackets and spaces). | BH1, GW1 L1 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | Also known as the Authorised Person. The named permit holder and / or landfill operator. | ABC Landfill Co. |
| Agency Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| No of Mon Points in Borehole | Total number of monitoring points in borehole. | 1, 2, etc |
| Sheet \_ of \_ | Sequential and total no of sheets used for this borehole record.  A continuation sheet (Table A1.1.b) completed for multiple monitoring points within a single borehole. | Sheet 1 of 3 |

**Table A1.1b: Group ID information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Multi Ref | Multiple monitoring point reference number.  The same reference number is used to link more than one monitoring installation within a single borehole or built structure. (Leave blank if not applicable). | BH1 |
| Cluster Ref | Cluster reference number.  A reference number used to group together a number of boreholes or wells drilled close together to monitor different vertical intervals.  (Leave blank if not applicable). | CL1 |
| Cell Ref | Landfill cell reference number.  A reference number used to group together a number monitoring points within a single hydraulically separate landfill cell. (Leave blank if not applicable). | Cell 1 |
| Area Ref | Site area descriptive reference.  Name or code used to group monitoring points geographically. | N (Northern site catchment)  SWB (South-western boundary) |

**Table A1.1c: Monitoring point ID information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Vertical sequence (from top): | Sequence of monitoring points in borehole from ground level downwards. | 1, 2, 3 etc. |
| Mon Point Ref: | Monitoring point reference number.  This should be an alphanumeric number which is unique at a particular site (avoid use of the characters: \*, /, \, -, \_, brackets and spaces). | GW1, L1 |
| SEPA Location Code | SEPA location code  (If available from SEPA). | 19373a01 |
| Mon Type | Type of monitoring installation. | LS (Long screened borehole)  Pz (Piezometer or shortscreened borehole)  C (Concrete ring) |
| Mon Use | Purpose of monitoring points  (Leachate, groundwater, gas, or some combination of these). | G (Gas monitoring only)  GW (Groundwater only)  GGW (Combined gas and groundwater monitoring)  L (Leachate monitoring)  GL (Combined gas and leachate monitoring) |
| Response zone | Name of zone being monitored. | WB Base of waste  WP Perched level in waste  GP Perched groundwater  GR Regional groundwater  AQ1 Aquifer 1 (Chalk) |
| Details on Sheet  No | Sheet number with monitoring point completion details.  For multiple monitoring points within a single borehole. | 1, 2, 3 etc |

**Table A1.1d: Construction record**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| SI BH Ref | Reference number of borehole at time of construction.  Use BH Ref No if separate number not used. Do not leave blank. | BH1 |
| Hole dia (mm) | Diameter of borehole in mm. | 150 |
| Hole depth (mbgl) | Depth to base of borehole recorded in borehole logs  Expressed as metres below ground level. | 18.35 |
| Date completed | Date of completion of borehole. | 15/6/01 |
| Contractor | Name of company undertaking construction | Mon Well Specialists Ltd |
| Supervisor | Name of company and competent person responsible for design and supervision | XY Consultancy, AB Smith |
| Construction method | Brief description of methodology used | Rotary hollow stem auger  Cable tool percussion  Rotary with air flush using down-the-hole hammer  SimCas / Odex |

**Table A1.1e: Ground survey at time of construction**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Surveyor | Name of company and competent person responsible for survey | YZ Surveyors, CD Jones |
| National Grid  Reference – Prefix | 100km Ordnance Survey Prefix | SO |
| National Grid  Reference – Eastings and  Northings | 12 Figure OS grid reference  Surveyed to at least 1m accuracy. The first number of the easting and northing identify the 100km grid square. A full 12 figure reference is essential to incorporate information reliably into GIS mapping systems. | 12 figure Grid Reference for Worcester City Centre:  385000 255000  Using the 100km prefix, this can also be expressed as:  SO 85000 55000 |
| Datum Point Description | Simple description of datum point used for water level measurements. | Top of external casing Top of internal lining |
| Height of datum (magl) | Difference in height between datum point and ground elevation  Expressed as metres above ground level. A “+” or “-“ symbol should be included to indicate height above (+) or below (-) ground level. | + 0.35, –0.07 |
| Datum elevation (m.AOD) | Surveyed elevation of datum point.  Expressed as metres above Ordnance Datum. | 95.42 |

**Table A1.1f: Lining completion record**

(Use continuation sheet to record details of multiple monitoring point within a single borehole)

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Lining material | Type of lining material used.  Use code or description | uPVC HDPE |
| Lining dia (mm) | Internal diameter of borehole lining expressed in mm. | 50 |
| Depth to base of lining (mbgl) | Depth to base of internal lining (or base of unlined borehole).  As recorded on original borehole log expressed in metres below ground level. | 15.67 |
| Top of lining (m.agl) | Height of borehole lining material above ground level.  Use negative number if level is below ground level. | 0.53, -0.06 |
| Screen description and size | Type and size of screen used.  Use code or description | 0.5mm slotted uPVC  2mm slotted uPVC with 250µm sock |
| Top of screen (mbgl) | Depth to top of screened interval expressed in metres below ground level. | 12.36 |
| Base of screen (mbgl) | Depth to base of screened interval expressed in metres below ground level. | 15.36 |
| Screen length (m) | Length of screened interval in metres (i.e. difference between top and base of screen). | 3.0 |
| Annular filter description and size | Use code or description for type and size of annular filter material. | 1 - 2mm rounded quartz sand and gravel  6mm pea gravel |
| Top of filter (mbgl) | Depth to top of filter material surrounding screen expressed in metres below ground level. | 11.85 |
| Base of filter (mbgl) | Depth to base of filter material surrounding screen expressed in metres below ground level. | 18.35 |
| Filter length (m) | Length of annular filter interval in metres (i.e. difference between top and base of filter). This is also known as the response zone. | 6.5 |
| Annular seal description | Use code or description for type and size of annular seal used. | Bentonite pellets / cementbentonite grout / coated bentonite pellets. |
| Top of seal (mbgl) | Depth to top of annular seal material above filter expressed in metres below ground level. | 9.75 |
| Base of seal (mbgl) | Depth to base of annular seal material above filter expressed in metres below ground level. (Should normally be the same value as Top of filter”). | 11.85 |
| Seal length (m) | Length of annular seal interval in metres (i.e. difference between top and base of seal). | 6.5 |

**Table A1.1g: Headworks**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Headworks description | Type and size of headworks used.  Use code or description | 200mm dia. raised steel cap  Manhole cover |
| Top of headworks (m.agl) | Height of headworks above ground level.  Use negative number if level is below ground level. | 0.65, -0.04 |

**Table A1.1h: Dedicated monitoring equipment**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Describe  equipment: | Brief description of any dedicated monitoring equipment within monitoring point | Pressure transducer for water level measurements  Dedicated pump (specify type) |

**Table A1.1i: Access and safety**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Describe | Notes describing any exceptional access or safety requirements for monitoring specific boreholes. | Walking access only over fence and 100m into field.  Strong venting of landfill gas, awkward height for sampling Gas protective masks and goggles needed. |

**Table A1.1j: Construction QC checks**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Dated: | Date details confirmed and filed in company records. | 31 July 2001 |
| Name of competent person | Name of competent person responsible for check. | JJ Jones |
| Position: | Position of named competent person | Monitoring manager External consultant or contractor (xyz Company Ltd) |
| Initials: | Signed initials of competent person. | JJJ |
| Borehole Log (Y/N) | Circle “Y” if a log recording drilling and geological details is available. “N” otherwise. | - |
| Lining Details (Y/N) | Circle “Y” if a log recording lining details is available. “N” otherwise. | - |
| QC Checks (Y/N) | Circle “Y” if information on logs has been QC checked. “N” otherwise.  Person responsible for QC checks should fill in details in this section. | - |
| SEPA Registered (Y/N) | Circle “Y” if monitoring point details have been submitted to SEPA. “N” otherwise.  Date should be date of submission. | - |

**Table A1.1k: Additional Fields on Table A1.1b (Borehole Multiple Record)**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Drop Tube Information (if any): (Leave fields blank if none) | | |
| Tubing Material | Type of lining material used.  Use code or description | Nylon, uPVC, HDPE |
| Tubing dia (mm) | Internal diameter of sample tubing expressed in mm. | 6 |
| Depth to base of tubing (mbgl) | Depth to base of drop tube recorded as depth below ground level. | 8.57 |

**Table A1.1l: Example borehole construction record sheet**

**Table A1.1l(a): Borehole Construction Record**

|  |  |
| --- | --- |
| **Borehole Reference Number** |  |
| **SEPA Permit Number** |  |
| **Site Name** |  |
| **Site Operator** |  |
| **No of Mon Points in Borehole** |  |
| **Sheet Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A1.1l(b): Group ID References**

|  |  |
| --- | --- |
| **Multi Ref** |  |
| **Cluster Ref** |  |
| **Cell Ref** |  |
| **Area Ref** |  |

**Table A1.1l(c): Monitoring Point ID Information**

| **Vertical Sequence (from top)** | **Mon. Point Ref No** | **SEPA database Ref No** | **Mon type** | **Mon Use** | **Strata** | **Details on Sheet No.** |
| --- | --- | --- | --- | --- | --- | --- |
| 1. |  |  |  |  |  | 1 |
| 2. |  |  |  |  |  |  |
| 3. |  |  |  |  |  |  |
| 4. |  |  |  |  |  |  |
| 5. |  |  |  |  |  |  |
| 6. |  |  |  |  |  |  |
| 7. |  |  |  |  |  |  |

**Table A1.1l(d): Construction Record**

|  |  |
| --- | --- |
| **SI BH Ref** |  |
| **Hole dia (mm)** |  |
| **Hole depth (mbgl)** |  |
| **Date completed** |  |
| **Contractor** |  |
| **Supervisor** |  |
| **Construction method** |  |

**Table A1.1l(e): Ground survey at time of construction**

|  |  |
| --- | --- |
| **Surveyor** |  |
| **Ground Elevation (m.AOD)** |  |
| **Easting (m)** |  |
| **Northing (m)** |  |
| **Datum point description** |  |
| **Height of datum (magl)** |  |
| **Datum elevation (m.AOD)** |  |

**Table A1.1l(f): Lining Completion Record**(use continuation sheet for multiple monitoring points in a single borehole)

|  |  |
| --- | --- |
| **Lining material** |  |
| **Lining dia (m)** |  |
| **Depth to base of lining (mbgl)** |  |
| **Top of lining above ground level (magl)** |  |
| **Screen description and size** |  |
| **Top of screen (mbgl)** |  |
| **Base of screen (mbgl)** |  |
| **Screen length (m)** |  |
| **Annular filter description and size** |  |
| **Top of filter (mbgl)** |  |
| **Base of filter (mbgl)** |  |
| **Filter length** |  |

**Table A1.1l(g): Headworks**

|  |  |
| --- | --- |
| **Headworks description** |  |
| **Top of headworks above ground level (magl)** |  |

**Table A1.1l(h): Dedicated Monitoring Equipment & Access and Safety**

|  |  |
| --- | --- |
| **Describe equipment** |  |
| **Describe special requirements for access or safety precautions** |  |

**Table A1.1l(i): Construction QC Checks**

|  |  | **Dated** | **Name of Competent Person** | **Position** | **Initials** |
| --- | --- | --- | --- | --- | --- |
| Borehole Log | Yes  No |  |  |  |  |
| Lining Details | Yes  No |  |  |  |  |
| QC Check | Yes  No |  |  |  |  |
| SEPA Registered | Yes  No |  |  |  |  |

**Table A1.1m: Example borehole multiple record sheet for multiple monitoring point details**

**Table A1.1m(a): Borehole Multiple Record Sheet**

|  |  |
| --- | --- |
| **Borehole Reference Number** |  |
| **Multi-Ref (if different to Borehole Reference Number):** |  |
| **Site Name** |  |
| **Site Operator** |  |
| **Ground Elevation at time of construction (m.AOD)** |  |
| **Sheet Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A1.1m(b): Monitoring Point Datum Description / Identification**

| **Vertical Sequence (from top)** | **Mon. Point Ref No** | **Datum Point Description / Identification Markings** |
| --- | --- | --- |
| 1. |  |  |
| 2. |  |  |
| 3. |  |  |
| 4. |  |  |
| 5. |  |  |
| 6. |  |  |
| 7. |  |  |

**Table A1.1m(c): Monitoring Point ID and Survey Information**

| **Vertical Sequence (from top)** | **1** | **2** | **3** | **4** | **5** | **6** | **7** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Mon. Point Ref No |  |  |  |  |  |  |  |
| Height of Datum (magl) |  |  |  |  |  |  |  |
| Datum Elevation (m.AOD) |  |  |  |  |  |  |  |

**Table A1.1m(d): Lining Information (if any) – Lining Material**

| **Lining material (description)** |
| --- |
|  |

**Table A1.1m(e): Lining Information (if any) – Lining Material**

| **Vertical Sequence (from top)** | **1** | **2** | **3** | **4** | **5** | **6** | **7** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Lining dia (mm) |  |  |  |  |  |  |  |
| Depth to base of lining (mbgl) |  |  |  |  |  |  |  |
| Top of lining above ground level (magl) |  |  |  |  |  |  |  |

**Table A1.1m(f): Lining Information (if any) – Screen**

| **Screen (description and size)** |
| --- |
|  |

**Table A1.1m(g): Lining Information (if any) – Screen**

| **Vertical Sequence (from top)** | **1** | **2** | **3** | **4** | **5** | **6** | **7** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Screen dia (mm) |  |  |  |  |  |  |  |
| Top of screen (mbgl) |  |  |  |  |  |  |  |
| Base of screen (mbgl) |  |  |  |  |  |  |  |
| Screen length (m) |  |  |  |  |  |  |  |

**Table A1.1m(h): Lining Information (if any) – Annular filter**

| **Annular filter (description and size)** |
| --- |
|  |

**Table A1.1m(i): Lining Information (if any) – Annular filter**

| **Vertical Sequence (from top)** | **1** | **2** | **3** | **4** | **5** | **6** | **7** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Top of filter (mbgl) |  |  |  |  |  |  |  |
| Base of filter (mbgl) |  |  |  |  |  |  |  |
| Filter length (m) |  |  |  |  |  |  |  |

**Table A1.1m(j): Lining Information (if any) – Annular seal**

| **Annular seal (description)** |
| --- |
|  |

**Table A1.1m(k): Lining Information (if any) – Annular seal**

| **Vertical Sequence (from top)** | **1** | **2** | **3** | **4** | **5** | **6** | **7** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Top of seal above filter (mbgl) |  |  |  |  |  |  |  |
| Base of seal above filter (mbgl) |  |  |  |  |  |  |  |
| Seal length (m) |  |  |  |  |  |  |  |

**Construction QC checks – See Front Sheet**

## A1.2 Monitoring point surveying and monitoring history record sheet for wells and boreholes

An example form is provided as Table A1.2. This form collates surveying and monitoring history information for each individual monitoring point. Where datum or positional information is updated for any reason (e.g. correction of previously estimated information, due to damage, or due to vertical extension), it is essential that proper records of these changes are maintained.

The following provides descriptions of information and examples applicable to each heading.

**Table A1.2a: Heading Information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Sheet \_\_ of \_\_ | Sequential sheet number for individual monitoring point. | 1 of 3 |
| Mon Point Ref | Monitoring point reference number.  This should be an alphanumeric number which is unique at a particular site (avoid use of the characters: \*, /, \, -, \_, brackets and spaces). | BH1, GW1, L1. |
| SEPA location code | SEPA location code (if available). | 19373a01 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number | WCC 123456 |

**Reference elevations from original construction logs**

See Tables A1.1a and A1.1b for description of each detail. All details can be converted to m.AOD using figures provided in Tables A1.1l and A1.1m. Subtract each detail expressed as mbgl from “Ground Elevation” to record m.AOD values.

**Table A1.2b: Surveying records**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Date of datum change | Date from which changes in survey details should be used. Since a survey may be carried out some time after this change has occurred it may mean some water level records have to be amended back to this date. | 2/1/01 |
| Date of survey | Date when ground survey was carried out. | 15/2/01 |
| Surveyed by | Name of company and competent person responsible for survey | YZ Surveyors, CD Jones |
| National Grid Reference – Prefix | 100km Ordnance Survey Prefix | SO |
| National Grid  Reference – Eastings and Northings | 12 Figure OS grid reference  Surveyed to at least 1m accuracy. The first number of the easting and northing are the 100km grid. A full 12 figure reference is essential to incorporate information reliably into GIS mapping systems. | 12 figure Grid Reference for Worcester City Centre:  385000 255000  Using the 100km prefix, this can also be expressed as:  SO 85000 55000 |
| National Grid  Reference – Status | Code indicating reliability of positional survey. | S (Surveyed)  GPS (GPS record)  E (Estimated from OS  Plan)  U (Unknown) |
| Datum Point  Details -  Description | Simple description of datum point used for water level measurements. | Top of external casing Top of internal lining |
| Datum Point  Details - Elevation (m.AOD) | Surveyed elevation of datum point.  Expressed as metres above Ordnance Datum. | 95.42 |
| Datum Point  Details – Relative to GL (magl) | Difference in height between datum point and ground elevation  Expressed as metres above ground level. A “+” or “-“ symbol should be included to indicate height above (+) or below (-) ground level. | + 0.35, –0.07 |
| Datum Point  Details – Ground  Elevation (m.AOD) | Ground Elevation.  Expressed as metres above Ordnance Datum | 95.07 |
| Datum Point  Details – Status | Code indicating reliability of level survey. | S (Surveyed)  E (Estimated)  U (Unknown) |
|  |  | 18.67 |
| Inits | Initials of competent person responsible for updating information. | AB Jones |

**Depth changes arising from change in datum point**

See Table A1.1 for descriptive details. The first record line should be for records taken from the original borehole log. Other lines are for when datum level has changed. It is important to know depths when undertaking sampling programmes. The most recent figures from this table can be used for updating the Site Monitoring Point Register (Table A1.3).

The “Date of Datum Change” is taken from the Surveying Record Table (above).

Details recorded as metres below ground level (m.bgl) are metres below the new ground level (if changed). This is calculated by subtracting the elevation of the detail from the ground elevation on the date of datum change.

Details recorded as metres below datum (m.bd) are metres below the new datum level.

This is calculated by subtracting the elevation of the detail from the datum elevation on the date of datum change.

**Monitoring History**

This table records significant dates relating to the collection of data for specific sets of monitoring measurements.

**Table A1.2c: Monitoring History**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| First Record | Date of first monitoring measurement. | 31 July 2001 |
| Initial  Characterisation  Completed | Date when initial characterisation record completed. | 31 December 2002 |
| End of Baseline (if reached) | Date recording when a specific monitoring data record is last used as a baseline record.  For data unaffected by landfill operations this record will remain blank. For leachate data this field will remain blank. | 31 December 2035 |
| No of Baseline Data Records | Total number of data records throughout baseline period.  Leave blank unless baseline is completed. | 16,250 |
| Last Record (if disused) | Date of last monitoring record.  This field should be filled-in for points which are no longer monitored for whatever reason. | 3 September 2004 |
| Comments | Any significant comments relating to monitoring history.  This could include the reference number of new monitoring point which may have replaced this one, or some significant influence on monitoring data. | Monitoring point replaced by GW99.  Water chemistry effected by road salting.  Groundwater level effected by dewatering from adjacent quarry in 1999 and 2000. |

**Table A1.2d: Example monitoring point surveying and monitoring history record**

**Table A1.2d(a): Monitoring Point Surveying and Monitoring History**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Monitoring Point Ref** |  |
| **SEPA database Ref Number** |  |
| **Sheet Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A1.2d(b): Reference Elevations (from original construction logs and ground survey at the time of construction)**

| **Date** | **Base of Borehole**  **m.AOD** | **Response Zone**  **Base of Filter**  **m.AOD** | **Response Zone**  **Base of Liner**  **m.AOD** | **Response Zone**  **Base of Screen**  **m.AOD** | **Response Zone**  **Top of Screen**  **m.AOD** | **Response Zone**  **Top of Filter**  **m.AOD** | **Top of Seal**  **m/AOD** | **Inits** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |

**Table A1.2d(c): Surveying Records – National Grid Reference (NGR)**

| **Date of Datum Change** | **Date of Survey** | **Surveyed by** | **NGR**  **Prefix** | **NGR**  **Eastings (6-fig)**  **(m)** | **NGR**  **Northings (6-fig)**  **(m)** | **NGR**  **Status** | **Inits** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **Original:** |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |

**Table A1.2d(d): Surveying Records – Datum Point Details (DPD)**

| **Date of Datum Change** | **Date of Survey** | **Surveyed by** | **DPD**  **Description** | **DPD**  **Elevation**  **m.AOD** | **DPD**  **Relative to GL**  **m.agl** | **DPD**  **Ground Elevation**  **m.AOD** | **DPD**  **Status** | **Inits** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Original:** |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |

**Table A1.2d(e): Surveying Records – Base of Lining**

| **Date of Datum Change** | **Date of Survey** | **Surveyed by** | **From new dip measurements**  **mbd** | **From new dip measurements**  **mbgl** | **Inits** |
| --- | --- | --- | --- | --- | --- |
| **Original:** |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |

**Table A1.2d(e): Surveying Records – Base of Lining**

| **Date of Datum Change** | **Base of Borehole**  **mbgl** | **Base of Borehole**  **mbd** | **Base of Filter**  **mbgl** | **Base of Filter**  **mbd** | **Base of Liner**  **mbgl** | **Base of Liner**  **mbd** | **Base of Screen**  **mbgl** | **Base of Screen**  **mbd** | **Top of Screen**  **mbgl** | **Top of Screen**  **mbd** | **Top of Filter**  **mbgl** | **Top of Filter**  **mbd** | **Top of Seal**  **mbgl** | **Top of Seal**  **mbd** | **Inits** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Original:** |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

**Table A1.2d(f): Monitoring History**

| **Monitoring Measurements** | **First Record** | **Initial Characterisation Completed** | **End of Baseline (if reached)** | **No of Baseline Data Records** | **Last Record (if disused)** | **Comments** |
| --- | --- | --- | --- | --- | --- | --- |
| Water levels |  |  |  |  |  |  |
| Water quality |  |  |  |  |  |  |
| Gas |  |  |  |  |  |  |
|  |  |  |  |  |  |  |

## A1.3 Monitoring point register for wells and boreholes

An example form summarising the main information that is required on a monitoring point register is provided as Table A1.3. This information can be extracted from individual monitoring point forms such as Tables A1.1 and A1.2 which should contain more specific detail for each monitoring point. The following provides descriptions of information and examples applicable to each heading.

**Table A1.3a: Heading Information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_\_ of \_\_ | Sequential page number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number | WCC 123456 |
| Mon Point Ref | Monitoring point reference number.  This should be an alphanumeric number which is unique at a particular site (avoid use of the characters: \*, /, \, -, \_, brackets and spaces). | BH1, GW1, L1. |
| Register Revision Number | Sequential number for updated registers. | Rev 1, Rev 2, Rev 3. |

**Table A1.3b: Data requirements**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Mon Point Ref: | Monitoring point reference number.  This should be an alphanumeric number which is unique at a particular site (avoid use of the characters: \*, /, \, -, \_, brackets and spaces). | GW1, L1 |
| Access & Safety (Note) | Footnote number describing any exceptional access or safety awareness details Leave blank otherwise. | 1, 2, 3. |
| Multi Ref | Multiple monitoring point reference number.  The same reference number is used to link more than one monitoring installation within a single borehole or built structure. (Leave blank if not applicable). | BH1 |
| Cluster Ref | Cluster reference number  A reference number used to group together a number of boreholes or wells drilled close together to monitor different vertical intervals.  (Leave blank if not applicable). | CL1 |
| Cell Ref | Landfill cell reference number  A reference number used to group together a number monitoring points within a single hydraulically separate landfill cell. (Leave blank if not applicable). | Cell 1 |
| Mon Type | Type of monitoring installation. | LS (Long screened borehole)  Pz (Piezometer or shortscreened borehole)  C Concrete ring) |
| Mon Use | Purpose of monitoring points  (Leachate, groundwater, gas, or some combination of these). | G (Gas monitoring only)  GW (Groundwater only) GGW (Combined gas and groundwater monitoring)  L (Leachate monitoring) GL (Combined gas and leachate monitoring) |
| National Grid  Reference – Prefix |  | SO |
| National Grid  Reference – Eastings and Northings | 12 Figure OS grid reference  Surveyed to at least 1m accuracy. The first number of the easting and northing are the 100km grid. A full 12 figure reference is essential to incorporate information reliably into GIS mapping systems. | 12 figure Grid Reference for Worcester City Centre:  385000 255000  Using the 100km prefix, this can also be expressed as:  SO 85000 55000 |
| National Grid Reference – S | Status code indicating reliability of positional survey | S Surveyed)  GPS (GPS record)  E (Estimated from OS  Plan)  U (Unknown) |
| Datum Point  Details -  Description | Simple description of datum point used for water level measurements. | Top of external casing Top of internal lining |
| Datum Point  Details - Elevation (m.AOD) | Surveyed elevation of datum point.  Expressed as metres above Ordnance Datum. | 95.42 |
| Datum Point Details – S | Code indicating reliability of level survey. | S (Surveyed)  E (Estimated)  U (Unknown) |
| Datum Point Details – Relative to GL (magl) | Difference in height between datum point and ground elevation  Expressed as metres above Ordnance Datum. | + 0.35, –0.07 |
| Depth of lining –  From BH Log | Depth to base of internal lining (or base of unlined borehole)  Recorded from original borehole log. Expressed as metres below new ground level and metres below new datum point. | 15.67 |
|  |  | 15.67 |
| Lining ID | Internal diameter of borehole lining Expressed in mm. | 50 |
| Screen - Top | Depth to top of screened interval.  Expressed in metres below ground level. | 12.36 |
| Screen – Base | Depth to base of screened interval.  Expressed in metres below ground level. | 15.36 |
| Response zone | Name of zone being monitored. | WB Base of waste  WP Perched level in waste  GP Perched groundwater  GR Regional groundwater  AQ1 Aquifer 1 (Chalk) |
| Access and Safety Notes: | Footnotes describing any exceptional access or safety requirements for monitoring specific boreholes.  Numbers correspond to those under “Access & Safety” column. | 1.Walking access only over fence and 100m into field.  2.Strong venting of landfill gas  3.Awkward height for sampling.  4.Gas protective masks and goggles needed. |

**Table A1.3c: QC checks**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Compiled by: | Name of person responsible for updating register. | JJ Jones |
| Checked by: | Name of person responsible for quality control or managing of monitoring programmes. | SS Smith |
| Position: | Position of named person | Monitoring manager External consultant or contractor (xyz Company Ltd) |
| Dated: | Date register completed. | 31 July 2001 |

## A1.4 Monitoring point register for surface waters and springs

An example form is provided as Table A1.4. Information requirements different to those on Table A1.3, with applicable examples, follow.

**Table A1.4a: Data requirements**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Water / leachate body | Name identifying water or leachate body being monitored. | River Thames  Northern ditch  Pond A  Leachate storage lagoon 1 |
| Area Ref | Name or code used to group monitoring points geographically . | N (Northern site catchment)  SWP (South-western boundary) |
| Mon Use | Purpose of monitoring points  Either leachate or surface water | SW (Surface waters)  LCH (Leachate) |
| Mon Type | Type of monitoring installation. | FS (Flowing water course)  Dr (Field drain discharge)  Spr (Spring)  Pd (Sample from pond or lagoon surface) |
| Description of monitoring point location | Exact location for sampling  Refer to plan or photo if necessary. | 10 m upstream of discharge  (access ramp on north side)  Inflow to manhole 2 (see plan ABC/123) |

**Table A1.4b: Example monitoring point register for boreholes and wells**

**Table A1.4b(a): Monitoring Point Register (Boreholes and Wells)**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Register Revision Number** |  |
| **Access and Safety Notes** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |
| **Compiled by (name and position)** |  |
| **Date Compiled** |  |
| **Checked by (name and position)** |  |
| **Date Checked** |  |

**Table A1.4b(b): National Grid Reference (NGR)**

| **Mon Point Ref** | **Access & Safety (Note)** | **Multi Ref** | **Cluster / Cell Ref** | **Mon Use** | **Mon Type** | **NGR**  **Prefix** | **NGR**  **Eastings (6-fig)**  **m** | **NGR**  **Northings (6-fig)**  **m** | **NGR**  **S** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |

**Table A1.4b(c): Datum Point Details (DPD)**

| **Mon Point Ref** | **Access & Safety (Note)** | **Multi Ref** | **Cluster / Cell Ref** | **Mon Use** | **Mon Type** | **DPD**  **Description** | **DPD**  **Elevation**  **m.AOD** | **DPD**  **S** | **DPD**  **Relative to GL**  **m.agl** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |

**Table A1.4b(d): Lining and Screen Information**

| **Mon Point Ref** | **Access & Safety (Note)** | **Multi Ref** | **Cluster / Cell Ref** | **Mon Use** | **Mon Type** | **Depth of Lining**  **From BH Log**  **m.agl** | **Lining ID**  **mm** | **Screen**  **Top**  **mbgl** | **Screen**  **Base**  **Mbgl** | **Strata** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |

**Table A1.4c: Example monitoring point register for surface water monitoring points**

**Table A1.4c(a): Monitoring Point Register (Surface Waters)**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Register Revision Number** |  |
| **Access and Safety Notes** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |
| **Compiled by (name and position)** |  |
| **Date Compiled** |  |
| **Checked by (name and position)** |  |
| **Date Checked** |  |

**Table A1.4c(b): National Grid Reference (NGR)**

| **Mon Point Ref** | **Access & Safety (Note)** | **Water / leachate body** | **Area Ref** | **Mon Use** | **Mon Type** | **NGR**  **Prefix** | **NGR**  **Eastings (6-fig)**  **m** | **NGR**  **Northings (6-fig)**  **m** | **NGR**  **S** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |

**Table A1.4c(c): Datum Point Details (DPD) and Monitoring Point Location**

| **Mon Point Ref** | **Access & Safety (Note)** | **Water / leachate body** | **Area Ref** | **Mon Use** | **Mon Type** | **DPD**  **Description** | **DPD**  **Elevation**  **m.AOD** | **DPD**  **S** | **DPD**  **Relative to GL**  **m.agl** | **Description of Monitoring Point Location** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |

# Appendix 2: Datum Point Identification and Measurement

## A2.1 Introduction

To express water level measurements to an accuracy of 1cm requires that a datum point is established on or near to each monitoring point. Ground level should not normally be used as a datum point unless this is a hard fixed surface with a distinguishing point of measurement. In general a datum point should be:

* Clearly identified in documentation and unambiguously distinguishable on the monitoring point, e.g. the top of the internal lining of a borehole or the top of external headworks and
* Surveyed by a competent person on final completion of the installation to a minimum accuracy of 0.5 cm and expressed in units of metres relative to Ordnance Datum level.

## A2.2 Surface water datum points

Where measurements of surface water level are taken the datum point should be either:

* An identifiable feature adjacent to the water body from which local levels can be subsequently resurveyed.
* An identifiable feature above the water body from which taped measurements can be taken or
* A fixed level board or other identifiable scaled feature within the water body.

## A2.3 Datum points for built leachate monitoring points

For monitoring points which are raised with the landfill, a permanent datum point cannot be accurately fixed until the structure is completed. This requires the use of temporary datum points and careful record keeping of structural changes.

A temporary datum point can be fixed at the base of the structure and then estimated by maintaining a record of the height of each raised section added. Alternatively, the base itself can be used as a temporary datum point. However, both situations can easily lead to erroneous results.

For example:

* Silt or other obstructions may block the base of the structure. (In this case any leachate level measurements which use the base as a datum would be recorded artificially low).
* The number and height of raised sections of the monitoring point can easily be mis-recorded or
* Built structures may become inclined during construction through waste requiring corrections to be made for the degree of inclination, which are unlikely to be sufficiently accurate.

The consequences of underestimating the datum level will be to record water levels lower than they really are. Conversely, any overestimate of datum level will result in water levels being recorded higher than they should be.

In the absence of a surveyed datum level, the potential for error can be minimised by confirming the depth to base of a built structure each time there is a change in datum. Where siltation of the base has occurred or where the monitoring point has become blocked for any reason, this check is not always satisfactory. An improvement in maintaining an accurate record of datum levels for built structures is possible by keeping clear records (See Table A1.2).

In summary, the following guidance is offered:

* The foundation of all monitoring points should be surveyed prior to commencement of infilling around the structure and expressed in metres above ordnance datum to an accuracy of 0.5 cm. This has the added benefit of confirming the base elevation of the structure in relation to the level of the site base, which is necessary for leachate level control.
* The top of each raised monitoring point should be surveyed at least annually during its construction and expressed in metres above Ordnance Datum to an accuracy of 0.5 cm.
* Whenever there is a change in datum level, the depth of the structure should also be measured for comparison to the original surveyed base level. If there are any major discrepancies which suggest the base may have become blocked contingency actions may be necessary to reinstate the monitoring point. In these circumstances it would be advisable to accurately survey the datum level of the monitoring point in order to confirm the need or otherwise for contingency measures and
* Where leachate levels are reported within databases or on paper records, the status of the datum point level measurement should be recorded as “Estimated” unless the datum point has been accurately surveyed (see For example, Table A8.4).

## A2.4 Datum points for groundwater monitoring points

Most groundwater boreholes once completed and surveyed should not undergo any significant movement. However, there will be occasions when datum points are moved – For example, due to damage, or due to the need to extend pipework vertically to accommodate re-profiling of surrounding land.

It is important to keep track of datum level changes for boreholes for the same reasons as those outlined above for built leachate monitoring points. In particular, the last two points are re-iterated:

* Whenever there is a change in datum level, the depth of the structure should also be measured for comparison to the original surveyed base level. If there are any major discrepancies, suggesting blockage of the screened interval, the datum level should be resurveyed as soon as possible and
* Where water levels are reported within databases or on paper records, the status of the datum point level measurement should be recorded as “estimated” unless it has been accurately surveyed (see For example, Table A8.4).

# Appendix 3: Leachate Monitoring Points Built During Landfilling

## A3.1 Types of built leachate monitoring points

Built leachate monitoring and abstraction points are structures which are progressively raised above a foundation within the landfill body at the same time as waste is landfilled.

The design of these structures is very varied within the industry, but can be categorised into three main types:

* Stacked ring structures. Typically 330 mm to 1m diameter thermoplastic or concrete rings. Variations include the provision of smaller diameter internal thermoplastic pipework which are either added and raised simultaneously within the larger diameter rings or installed in entirety on completion.
* Telescopic or jointed pipe structures. These are thermoplastic pipe lining systems, typically 300 mm to 600 mm diameter. Proprietary telescopic systems consist of 3m pipes extendable on slip joints to a total length of 4 to 5m. Additional sections are attached using couplings and
* Welded Structures. These are not so commonly used but typically consist of 6m lengths of 300 mm steel pipework welded together as the landfill is raised.

## A3.2 CQA and monitoring objectives

All structures built within a landfill which are to be used for monitoring purposes should be based on the following minimum CQA and design requirements:

* The objectives of the monitoring point should be clearly stated in advance of construction, and its design tailored to meet these objectives.
* CQA procedures should be adopted to document the design, construction and maintenance of the monitoring point.
* The possibility of failure of a number of built monitoring points should be considered. It may be appropriate to allow for the construction of additional monitoring points to cover this possibility. A feasibility assessment for retro-fitting monitoring structures should be provided and
* The completion details for headworks should accommodate the needs of monitoring personnel. It is common for built monitoring structures to have multiple uses (e.g. leachate and gas extraction). In designing headworks, due consideration should be given for safe access for monitoring personnel including allowance for the use of any designated monitoring equipment.

## A3.3 Construction design features

Key design features include the following:

* Foundations. i.e. foundation design and structural support needed to, support weight and avoid puncturing the landfill lining system.
* Structure. i.e. materials and features required to maintain verticality and prevent collapse or damage.
* Means of leachate entry. i.e. selection of appropriate location and type of openings to meet the monitoring objectives. and
* Headworks design. i.e. allowing safe access for monitoring, and facilities to carry out the monitoring specified in the objectives.

## A3.4 Foundations

### A3.4.1 Foundations

Foundations are needed to adequately support the weight (including settlement pressure) of any built structure, to maintain verticality, and to avoid damage to underlying materials. Two circumstances arise:

* Structures sited directly on the site base. A level, load-bearing foundation is required and
* Structures sited at higher levels within waste.

Less stringent engineering measures may be acceptable, depending on the depth of waste below the structure and the ultimate height of the structure.

In all cases, engineering calculations should be provided to confirm the load-bearing capability of the structure and its long-term stability.

## A3.5 Structure

### A3.5.1 Maintaining vertically during construction

Maintaining verticality in built structures is one of the more difficult practical problems associated with all types of built leachate monitoring structures. Particular problems arise when pipes have to be extended to large depths (e.g. greater than 20m) or where pipework emerges through temporary sidewalls or terraces.

The chances of pipework remaining vertical can be increased by:

* Using a secure coupling method to ensure successive sections of pipework are fixed vertically and will not slip laterally.
* Using a means to measure and maintain verticality of newly installed sections and
* Installing within a protective outer liner to prevent disturbance by machinery.

After installation, verticality is maintained by design features which minimise shear and settlement, as described in the following section.

### A3.5.2 Preventing shear and settlement damage

In order to reduce the potential for damage due to settlement and lateral movements of waste, structures ideally need to be protected externally in two ways:

* Protection from the downward force of waste settlement. Achieved by the use of a smooth outer surface (collar couplings should be avoided), and by use of a slip medium, generally a loosely compacted granular material immediately surrounding the stacked or telescopic pipework and
* Protection from lateral movements. Achieved by use of a well-compacted granular material or other strong material surrounding the slip medium.

Constructing these two concentric layers in granular materials is generally impractical on most landfill sites. Many operators overcome this difficulty by using a sacrificial outer liner (e.g. concrete ring) with a granular material used to infill the annular space between this and the main riser pipe.

### A3.5.3 Lining materials

Lining materials need to be able to cope with significant lateral stress caused by waste movement, the chemistry of the leachate and, sometimes, high temperatures. (Biodegrading domestic wastes can produce temperatures in excess of 30 degrees centigrade. Fires in landfill sites do occasionally occur). These issues should be the prime consideration in selecting materials.

Lining materials in use include:

* Concrete rings. Concrete must be designed to take account of leachate quality (some leachate may be of low pH and high in sulphate and chloride, all of which are aggressive to cement), weight of overlying rings in finished structure, and need for holes / porous sections (which are structurally weaker) to allow leachate ingress.
* Plastics. Polypropylene, high and medium density polyethylene (MDPE and HDPE) and poly-vinyl chloride (PVC) have all been used with success. Pipe should be flush jointed or telescopic, of a grade suitable to withstand collapse pressure, lateral movement and weight of overlying sections in finished structure. Likely temperature range should also be considered and
* Steel. Usually meets strength requirements, but consideration needs to be given to possible corrosion problems, depending on leachate quality.

## A3.6 Means of leachate entry

### A3.6.1 Size and type of granular surround materials

Granular material in landfill sites, particular drainage media, needs to be sized to minimise bio-fouling. In practice larger gravel sizes have been found to be preferable for this purpose. Typical sizes in use include:

* 18 – 32 mm diameter.
* 16 – 40 mm diameter and
* 40 mm diameter.

Further guidance on design of drainage media is given in landfill design guidance (e.g. Waste Management Paper 26B).

Non calcareous materials are often specified for granular layers, due to the possibility of dissolution of calcite in acidic leachate, followed by long term precipitation in pores or pipe openings in the drainage system.

### A3.6.2 Size and distribution of openings

The size and position of openings or machined slots in external and internal linings should be determined in relation to the objectives of the monitoring point:

* For built structures which are to be utilised for gas extraction. Openings may be required throughout the majority of its length to maximise gas collection.
* For built structures which are to be utilised for leachate dewatering Openings are probably required at the base (particularly if a drainage layer is present) and may be required higher in the waste and
* For built structures which are intended to record the level of leachate at the base of the site. Openings may only be necessary in the lower part of the structure.

The size of openings should be less than the size of surrounding granular material but not so small as to be easily blocked by bio-fouling or solid materials. Opening sizes vary according to practical experience by different operators. Some reported sizes and spacings for concrete rings are:

* 0.5 cm diameter holes, 4 to 6 holes per circumference, spaced 10 cm to 35 cm vertically and
* 3 cm diameter holes, spaced every 25cm around the circumference and 50 cm vertically.

Internal linings can include holed pipework or machine-slotted pipework which typically range in size from 1 mm to 5 mm slot size. Some operators prefer to use drilled holes similar to those in external concrete rings to minimise clogging or biofouling.

## A3.7 Headworks design considerations

Structures built through landfill sites often have multiple uses, which can lead to conflicting requirements. These will dictate the complexity of the headworks design. For example,:

* If used for gas extraction, it is important to provide an air-tight seal to avoid drawing oxygen from the atmosphere into the system when under suction.
* In order to control leachate levels, a pump may need to be temporarily or permanently installed.
* For gas monitoring, gas taps will be needed.
* For measuring leachate levels with conventional dip meters an access port will be needed. Measurements may need to be taken when both gas suction is off (i.e. an isolating valve needs to be accessible) and the leachate pump is not operating and
* For measuring leachate levels, a procedure is needed for establishing and recording measurement datum each time a new section is installed. See Appendix 2 (Section A.2.3).

# Appendix 4: Borehole Drilling Methods

## A4.1 Introduction

Information in this chapter is based on Environment Agency Research and Development Documents and are drawn from a variety of other sources, including the Site Investigation Steering Group (1993) and Blakey et al. 1997.

## A4.2 Design issues

### A4.2.1 Drilling close to or into the base of a landfill

When drilling to the base of any landfill site a decision needs to be taken whether or not it is safe to drill to the base of waste in order to provide a good leachate monitoring point. This is clearly not a sensible option if the elevation of the base is not known exactly and consists of, For example, an artificial liner of limited thickness.

In sites which are underlain by a significant thickness of natural low permeability material it may be possible to drill a short distance into this layer with the agreement of SEPA. This would need to be assessed on a site-specific basis in relation to risk. Where risks are unacceptable or insufficiently defined, drilling through the base should be avoided.

In order to avoid puncture, boreholes should not normally be drilled into waste any closer than 3 metres above the site base unless precise survey information is available and borehole drilling depths can be carefully controlled and certified by independent supervision. In all cases ground elevations and position should be confirmed before and after drilling. The competent person responsible for specification of the drilling contract should ensure that the liabilities and contingency measures to be adopted in the event of puncturing the site base are clearly established in advance of drilling works.

If the basal lining (natural or engineered) of a site is accidentally punctured during drilling this should be reported immediately to SEPA and contingency measures implemented to seal the base of the hole to minimise leachate leakage. Additional assessment monitoring and remediation measures may need to be initiated as a result of such incidents.

### A4.2.2 Precautions to avoid borehole collapse during drilling in waste

The specification for construction of a leachate monitoring point should include the depth to the base of installed lining within the drilled borehole. The contractor should be made aware of this specification in advance of tendering for the work so that appropriate drilling techniques can be used to ensure that the depth specified is achievable and can be certified by measurement by the person responsible for supervision of the contract.

When drilling in waste, particularly below leachate level, the side walls of the drilled hole may become unstable and collapse. In these instances, either temporary casing (or possibly drilling fluid) may be needed to support the side walls during drilling to allow lining to be installed into a clean open hole on completion. Whilst it may be possible to install a lining below leachate level without the need for temporary casing, the possibility of collapse should be considered, particularly if there is no history of drilling for the site. Where collapse occurs in unlined boreholes, it may be necessary to over-deepen the borehole in order to achieve specified lining depths. Where there is doubt as to the likely success of open hole drilling methods, back-up procedures should be clearly specified to provide formation support in the event that lining depths are not achieved.

Drilling methodologies which are capable of utilising temporary casing include:

* Cable tool percussion (“shell and auger”).
* Rotary hollow stem augers and
* Specialist rotary drilling systems (e.g. “Odex” or “SimCas” -see below).

Alternatively the same objective can be achieved by utilising two drilling rigs. For example, a continuous flight or single flight rotary auger can be used to drill through the waste and to clear obstructions followed by a cable tool rig to clean-out and provide temporary casing to support the side walls during installation of the monitoring point lining.

### A4.2.3 Selecting depth and diameter of boreholes in waste

Before specifying a drilling methodology for waste, a clear specification of the depth and diameter of the completed monitoring installation is required.

For monitoring purposes, smaller diameter installations (typically between 100 mm and 300 mm) are preferred. If an annular gravel pack and surface seal are to be installed around a lining, the borehole needs to be drilled at a diameter which is ideally 100 mm or greater than the outside diameter of the lining material. For example, to install a 150 mm diameter lining with a gravel pack usually requires a hole diameter of 250 mm or greater. Where a gravel pack is not needed (For example, for installations within hollow stem augers) a drilled hole slightly wider than the final lining is adequate, though this assumes that the formation will readily collapse around the final lining on withdrawal of the augers.

Some considerations in selecting a borehole and lining diameter follow:

* Larger diameter installations (over 300mm in diameter) are not ideal as monitoring points for obtaining appropriate leachate quality samples due to the accumulation of large volumes of standing water, which may require purging before samples can be taken. They can be good monitoring points for sampling if they are regularly pumped for other reasons (e.g. for leachate level control), but in this case they would not necessarily make good leachate level monitoring points.
* To construct boreholes capable of accommodating large diameter linings, particularly at greater depths requires the use of very large drilling or piling rigs. Such equipment can be costly and problematical to employ on landfills. Drilling at any diameter below 25 to 30m depth in waste is particularly difficult.
* Installations smaller than 100 mm diameter can be utilised for monitoring in waste, though these are probably only suitable in relatively shallow sites (probably no greater than 10 m depth) where they are less likely to be damaged by waste movement. Linings of 100 mm diameter or larger usually have greater strength to resist lateral forces exerted by settlement and lateral movements of waste and
* If monitoring points are also to be used for dewatering or for gas extraction they need to be of sufficient diameter to accommodate pumps (dewatering pumps typically require a minimum hole diameter of 100 mm). The optimum lining diameter for leachate monitoring and control purposes is probably 125 to 150 mm.

### A4.2.4 Selecting depth and diameter of boreholes in natural ground

It should not be assumed that boreholes should simply be drilled to a depth governed by the depth of waste in the adjacent landfill or any other rule of thumb. The depth of drilling should be specified in the light of an understanding of hydrogeological conditions and the physical characteristics of the underlying strata. Every site setting is unique. A competent professional should undertake specification of drilling depths for groundwater monitoring boreholes.

The depth of drilling should take account of factors which should have been assessed by knowledge accumulated from prior site investigation including the following:

* Knowledge of the depth and lateral extent of the groundwater system to be monitored. If this lies below perched or other groundwater systems, steps need to be taken to ensure a seal is maintained between systems both during drilling and following installation of the monitoring point.
* Knowledge of the likely depth and seasonal variation in water table in unconfined groundwater systems. Normally drilling should continue below the lowest level of seasonal water table variation, to a depth sufficient to allow adequate purging and sampling.
* Knowledge of the most likely depth of contamination arising from the landfill site. This will vary depending on factors such as where exactly contamination enters the groundwater system, how far down-gradient of the site the monitoring point is located and the hydraulic characteristics of the groundwater system. For example, in a flood plain there is often a component of groundwater movement vertically upwards which can be the result of discharges to surface water so that monitoring points can probably be designed to relatively shallow depths. Conversely, a landfill on a hill top may require deeper monitoring points due to the tendency for groundwater to move vertically downwards and
* Knowledge of the vertical distribution of contamination. This may require the provision of multi-level, nested or clustered boreholes.

## A4.3 Drilling methods

### A4.3.1 Health and safety

Waste materials are highly variable and potentially hazardous. Guidance issued by the Institute of Civil Engineers Site Investigation Steering Group, 1993 for safe drilling in wastes should be followed. Most landfills will be designated as high or medium risk drilling environments (category “red” or “yellow”) and contracts with drilling companies should make proper allowance for the necessary procedures and equipment needed to complete works safely.

Drilling of monitoring boreholes adjacent to landfill sites can be equally hazardous as a result of gas or leachate migration. Special precautions may need to be taken to ensure the safety of drilling personnel.

### A4.3.2 Drilling in waste

The most commonly used conventional drilling methods are:

* Continuous flight augers.
* Single flight augers.
* Hollow stem augers.
* Cable percussion (shell and auger) and
* Large diameter single-tube barrel.

Due to the dangers of bringing contamination in the flushing medium in contact with personnel at ground surface, the use of conventional rotary drilling rigs in waste is not recommended (Site Investigation Steering Group, 1993). The use of air as a flushing medium in waste is particularly hazardous and should be avoided, unless the dispersion of air can be fully controlled at the well head.

Some drilling programmes have been successfully completed using more than one type of drilling rig. For example, it is possible to drill through waste using a continuous or single flight auger at 300 mm diameter. A percussion rig can then be used to clean out and support the hole using 250 mm diameter tools and temporary casing. A 150 mm diameter lining can then be installed. This type of method has been used successfully for installations up to 30m deep.

### A4.3.3 Drilling natural ground

The choice of drilling method and equipment employed should be made on a site-specific basis whilst considering the following:

* Depth and diameter of drilling required and likely depth of first water strike.
* Ability to penetrate the formations anticipated.
* Degree of contamination anticipated.
* Ability to obtain samples and identify different formations.
* Ability to identify groundwater inflows.
* The extent of disturbance to ground materials during drilling.
* The impact of drilling technique on groundwater quality and
* Ability to undertake in-situ testing and to install monitoring equipment.

The most commonly used drilling methods are:

* Conventional rotary drilling.
* Cable percussion (shell and auger) and
* Augers (hollow stem, continuous flight or single flight).

A summary of advantages and disadvantages of conventional drilling methods is presented in Table A4.1 and a brief description of each and their suitability for monitoring well installation given in the following sections.

**Table A4.1: Advantages and disadvantages of drilling methods for monitoring borehole installations**

| **Drilling method** | **Advantages** | **Disadvantages** |
| --- | --- | --- |
| Cable tool | * Inexpensive. * Easily cleaned. * Easy to identify lithological changes and water strikes. * Bulk and undisturbed (“U100”) samples. * Possible minimum use of drilling fluids and * Use of temporary casing allows accurate installation of lining and annular fill. | * Slow. * Cannot penetrate hard rock and * Can smear sides of borehole. |
| Rotary auger | * Rapid. * Inexpensive. * Easily cleaned. * Hollow stem augers allow continuous sampling in unconsolidated materials. * Lining can be installed directly into hollow stem augers and * No drilling fluids needed. | * Cannot penetrate hard rock. * Hollow stem augers cannot penetrate where cobbles or boulders are present. * Sampling depth and water strikes difficult to identify using solid stem augers. * Solid stem augers cannot be used in loose ground (hole collapses) and * Unable to install annular fill and seals in collapsing ground. |
| Other rotary methods | * Can be inexpensive. * Fast in consolidated materials. * Can be adapted to drill all formation types and * Continuous samples can be cored in consolidated rock and clay. | * Can be expensive. * Fluids need to be added (e.g. air, foam, water, mud). * Possible introduction of contaminants (including oil from air compressor) with circulating fluid. * Recovery of samples can be slow when drilling at great depths. * Can smear sides of borehole and * Synchronous casing methods in unconsolidated formations only allow installation of narrow diameter lining. |

### A4.3.4 Cable tool percussion boring

The percussion, cable tool, or “shell and auger” method as it is commonly referred, is simple, versatile and relatively inexpensive. This method, as the name implies, involves the lifting and dropping of different tools in order to break, penetrate and remove the soil/rock formations encountered.

A typical site investigation rig consists of a winch, which is normally powered by a diesel engine, and an A-frame or derrick of about 6m in height. Larger rigs designed for deeper drilling or large diameter drilling (For example, for pile installation) are also available. In soft formations temporary casing has to be driven down as drilling proceeds in order to support the sides of the borehole. To achieve progress it is sometimes necessary to add water to the borehole during boring.

Temporary steel casing is usually inserted to ensure that the borehole remains stable during boring operations. This also serves to reduce cross contamination from groundwater at different horizons.

Site investigation rigs are suitable for drilling in unconsolidated materials including waste. In very loose materials such as wet sand and gravel formations, drilling progress can be very slow. Obstructions such as large boulders, metallic objects, tyres and even an accumulation of filled plastic bags, which cannot be removed by chiselling can lead to abandonment of the borehole. In these cases either a further hole has to be attempted in another location or an alternative drilling method used. In deeper holes the temporary steel casing can become jammed in the borehole requiring the slow process of hydraulic jacking to remove it.

Larger percussion rigs are capable of penetrating consolidated materials, and drilling at larger diameters.

### A4.3.5 Solid stem continuous flight rotary auger drilling

This drilling rig comprises of a drill mast normally 3 to 6 m high and a hydraulically powered rotating continuous flight auger. The drilling rods are helical and are effectively screwed into the ground. The technique does not require a flushing medium such as water or air. Auger sections are usually connected by key and pin mechanisms and do not therefore require lubricants. Inclined boreholes can be drilled, subject to the nature of the formation.

Following completion of the drilling operation, the auger has to be withdrawn from the hole before lining materials can be installed. This can sometimes lead to borehole instability particularly within saturated ground. In general, continuous flight augers are of limited use when drilling in very soft, fine-grained soils, in "clean" granular soils and in almost all soils below the groundwater level.

Augers are commonly used in waste because of their ability to progress rapidly through ground which cable tool rigs would either take a long time to drill or become obstructed. However, shredded articles and particularly wire may become entangled around the augers and in some circumstances may be left bridging the borehole This can lead to difficulties with lining installations.

It is important to note that it is nearly impossible to drill through a contaminated soil zone with a solid-stem continuous flight auger without transporting contaminants downwards.

### A4.3.6 Hollow stem continuous flight rotary auger drilling

This system of drilling is very similar to the technique described above but with the key difference being that all down-hole tools are constructed around a hollow tube through which sampling, testing and placement of borehole instrumentation can be achieved. The technique does not require water or air flushing media, nor do joints need to be greased. Most conventional hollow stem augers have an internal diameter of less than 125mm allowing lining diameters of no greater than 100mm diameter to be installed. The drilling rods are considerably heavier than conventional rotary tools and consequently the depth of drilling is more limited.

### A4.3.7 Other rotary drilling methods

Rotary drilling provides a technique which uses a variety of rock cutting tools mounted at the end of a drill pipe of smaller dimension. The drill pipe is rotated mechanically. Cuttings can be brought to the surface by the tool itself or more commonly by means of a circulating fluid. This drilling technique is suitable for use in stable ground to depths in excess of 50 metres and is often the only viable drilling method when penetrating hard formations.

The circulating fluid is generally delivered through the drill pipe before it passes through the drill bit and then upward between the annular space between the borehole wall and the drill rod. The types of flushing media commonly employed include air, water, foam, mud, bentonite, polyacrylamide, guar and xanthan. Air and water are most commonly used for contaminated land investigations. The use of air as a flushing media when drilling in waste is not recommended by the Site Investigation Steering Group, 1993 for safety reasons.

All drilling fluids will to some degree invade the formation and therefore could contaminate and interact with the surrounding formation. When air is used as the medium, the potential for chemical interaction with groundwater or leachate must be carefully considered. Large quantities of air may be introduced into the borehole, (2040 cubic metres per minute), and experience shows that air entrapment in groundwater may occur several hundreds of metres from the borehole being drilled. Furthermore, compressor oil often becomes entrained within the air stream which can lead to temporary hydrocarbon contamination within the borehole.

With both mud and air rotary drilling, lubricants must be used on the drill pipe to make it easy to thread together and take apart during drilling. Standard lubricants should not be used because they contain petroleum hydrocarbons and heavy metals. A Teflon based lubricant is available for use, and food-grade lubricants used on food processing machinery can also be used without presenting the potential for contaminating the borehole. At the termination of drilling each borehole the fluid must be recovered.

Conventional rotary drilling methods are generally quicker than other methods but require larger drilling rigs which may not be able to gain access to all areas of a site.

### A4.3.8 Other methods

There are numerous other methods used to install monitoring boreholes, particular at shallow depths. These methods must be considered both in terms of their ease of operation and their applicability to meeting information objectives. Where novel methods are used, prior consultation with the Environment Agency should takes place to assess their effectiveness against the objectives of the drilling programme.

## A4.4 Sources of contamination

### A4.4.1 Addition of water during drilling

It is sometimes necessary and unavoidable for water to be added either as a circulating fluid for rotary drilling or to loosen up unconsolidated materials in percussion drilling. Where water is added it must come from a source of known quality. Where critical, a sample and analysis of the added water should be provided as a reference against water samples recovered from the borehole during drilling or from monitoring installations.

### A4.4.2 Decontamination of equipment

All equipment used for drilling into waste should be thoroughly cleaned at the start and on completion of works. As a basic minimum, all equipment should be washed down using a steam cleaner. Other decontamination procedures may be necessary if contact with specific hazardous substances occurs or is anticipated.

If boreholes are being drilled into uncontaminated strata, decontamination between each borehole may be necessary. This may simply consist of rinsing, pressure washing or steam-cleaning parts of equipment which are used down-hole. If the rig has been used within contaminated ground the complete recirculation system of the drill rig must be thoroughly cleaned and de-contaminated before moving to the next borehole location. In some instances quality control measures should be introduced to certify the cleanliness of the equipment. These should be reviewed in advance with SEPA.

### A4.4.3 Disposal of drilling materials and fluids

Borehole drilling and development can produce large quantities of water which requires disposal. Prior to disposal, silt should be removed from water by use of a series of simple settling tanks. If chemically contaminated, advice should be sought from SEPA for safe disposal prior to commencement of works.

Drill cuttings and settled solids may also be contaminated, in which case arrangements may need to be made for disposal at an appropriately licensed facility.

## References

Aller, L., Bennett, T.W., Hackett, G., Petty, R.J., Lehr, J.H., Sedoris, H., Nielsen, D.M., and Denne, J.E. (1989). *Handbook of suggested practices for the design and installation of ground-water monitoring wells*. National Water Well Association. USA. Ref: EPA 600/4-89/034 1989.

Brandon, T.W. (1986). *Groundwater occurrence, development and protection*. Water Practices Manuals. 5. Institution of Water Engineers and Scientists. ISBN: 0-901427-14-4.

British Standards Institution (1999). *British Standard BS5930: Code of practice for site investigations*. London.

Cox, S. and Powrie, W. (2000). *Horizontal wells for leachate control in landfills*. Wastes Management, December, 35-37.

Driscol, F.G. (1986). *Groundwater and wells*. St Paul, Minnesota, Johnson Division. USA

Environment Agency (2000). *Groundwater and contaminated land project: Technical aspects of site characterisation*. Environment Agency. Report No. R&D Technical Report HOCO-373.

Site Investigation Steering Group (1993). *Guidelines for the safe investigation by drilling of landfills and contaminated land. Site investigation in construction series. Volume 4*. Thomas Telford Services Ltd. London.

# Appendix 5: Borehole Completion Details

## A5.1 Introduction

There are no guidance documents in the UK which provide specific details relevant to the design and installation of monitoring boreholes. Outline details for piezometer and long-screened (“standpipe”) installations are described in BS5930 and other geotechnical references. Detailed guidance relevant to water well drilling is available from texts such as Driscoll, 1986 and Brandon, 1986. UK research on aspects of monitoring borehole design is summarised in Blakey et al, 1997 (Appendix C4) and referenced in relevant sections below. More detailed manuals are available from USA including Aller et al, 1989 which specifically deals with the design and installation of monitoring boreholes.

The following appendix draws some general information from these and other sources, though for much greater detail, the original documents are best consulted.

## A5.2 Design considerations

### A5.2.1 Use of unlined boreholes for monitoring

Boreholes drilled into competent[[22]](#footnote-22) strata may in some instances be completed without the need for lining. Any boreholes completed as open holes require the upper section of the borehole to be sealed from ground surface by the installation of steel casing of at least 1m length which is grouted in place.

The depth of such boreholes should however be limited in accordance with general guidance given in this document which requires that long screened or open boreholes should not normally be greater than 10m deep and only used where groundwater flow is primarily horizontal.

### A5.2.2 Diameter of completed installation

The internal diameter of a completed installation should be sufficient to accommodate designated monitoring equipment for sampling and water level measurements.

Most boreholes constructed for monitoring purposes are typically completed with linings ranging in diameter between 19 mm and 200 mm, though some multi-level installations incorporate individual sampling lines as small as 6 mm in diameter.

For general groundwater monitoring purposes it is recommended that the completed lining diameter should normally be between 50 and 200 mm. Larger diameter installations are not ideal for obtaining appropriate groundwater or leachate samples unless they are regularly pumped or are sampled using depth samplers. Smaller diameter installations may not be ideal for combined sampling and water level measurements, and in low yielding formations may not be capable of yielding sufficient sample volume for laboratory analysis.

Smaller diameter (less than 50 mm diameter) installations should not be dismissed, particularly since these are increasingly being developed both for research and commercially in order to enable better vertical characterisation of groundwater. However, where these are used, technical justification should be provided including specification of monitoring objectives and the monitoring equipment to be employed.

### A5.2.3 Influence of well construction materials and sampling equipment on water quality of samples

The following text is paraphrased from Blakey et al. 1997, Appendix C4:

* Any construction material or sampling equipment which comes into contact with the water sample being collected, can affect the integrity of the sample by leaching compounds into solution, by the adsorption (and subsequent desorption) of compounds from the solution, by gas diffusion through the material and also by solute transfer.
* Most studies (e.g. Baxter, 1982, Barker et al., 1987) have concentrated on the adsorption and subsequent desorption of volatile solvents from plastic pipework and not the inorganic constituents of groundwater.
* The general advice when sampling for organic compounds is to use either polyethylene, polypropylene or PTFE (“Teflon”) tubing which all have a hard surface, in preference to soft rubbers and plasticiser containing plastics which have a greater tendency to adsorb and leach volatile compounds and
* Standardisation of borehole construction and sampling techniques at any one site are desirable.

## A5.3 Lining materials and screens

### A5.3.1 Selection of lining material in waste

Materials used to line monitoring boreholes in waste need primarily to cope with potentially high temperatures and significant lateral stress caused by waste movement. These issues tend to override any other design concerns such as the absorptive / desorptive properties of the lining material.

Suitable lining materials include high and medium density polyethylene (MDPE and HDPE) and poly-vinyl chloride (PVC). Other materials such as steel and polypropylene have also been successfully used.

### A5.3.2 Selection of lining material in natural ground

For groundwater monitoring, suitable borehole linings include stainless steel, high and medium density polyethylene (HDPE and MDPE), and poly-vinyl chloride (uPVC). For general monitoring purposes uPVC and polyethylene (PE) are practical and economical. Stainless steel or more inert plastics such as tetrafluoroethylene (teflon or TFE) may sometimes be preferable for specific contamination studies.

Lining with flush-threaded pipe joints, which leave a smooth bore on both the inside and outside of the joined pipes is preferable to the use of any other coupling methods. Flush threads provide smooth internal and external surfaces which enable annular filters and seals to be installed more readily and also simplifies the use of sampling equipment.

The use of solvent-based glues for attaching joints or any other use in a borehole should be avoided.

### A5.3.3 Selection of borehole screens

A properly designed borehole screen serves the purpose of allowing water to flow into the borehole whilst minimising the amount of sediment inflow, particularly when used in conjunction with a gravel pack. Many screens can be supplied in a variety of slot sizes and may also incorporate filter wraps to reduce the size of openings. In water well design, it is possible to relate slot size to the formation being screened to ensure that silt is removed from the formation during development of the well to produce a clear inflow of water. Monitoring boreholes around landfills may be located in low permeability and fine-grained formations which contain proportionately greater amounts of silt and clay particles than are commonly found in aquifer systems used for water abstraction. This can lead to difficulties in completely removing sediment from all samples.

**Screen aperture**

Screen apertures should be selected to minimise fine particles entering the borehole and to optimise flow into the borehole at a velocity which will not cause undue turbulence.

For monitoring boreholes in very fine formations (e.g. predominantly silts or clays) it is very difficult to achieve either of these objectives. If the formation grain sizes are at or below fine sand (0.2 mm) the use of small slots (e.g. 0.25 or 0.5 m), will do nothing to stop particle entry, but may actually increase entrance velocities and encourage entrainment. If a very small slot size is achieved (e.g. by use of a geotextile wrap) there is a risk of clogging. In these situations, the use of a filter pack (e.g. 0.5 to 2 mm grain size) with as wide an annulus as possible around the screen should be encouraged, rather than reducing the slot size to a point where clogging may occur. Particular care with well development is necessary in these constructions (see Appendix 6).

For monitoring wells in sandy or coarser formations, the slot size and screen may be based on water well design principles (e.g. Driscoll, 1986, Aller et al, 1989).

For monitoring boreholes in waste, the selection of a screen slot size is often governed by the selection of lining material. Some plastics (e.g. HDPE) can only be cut with relatively coarse slots (typically 3 mm) whilst PVC can be machine-cut to 0.25 mm or smaller. Slot sizes are not so critical as in natural ground, except where the waste is composed of a significant proportion of unconsolidated material. In these cases a gravel pack or a geotextile wrap around the screen can be beneficial.

**Screen length**

Screen lengths should normally be no greater than 6m and ideally shorter than this. Where it is necessary to screen strata for intervals in excess of 10m, separate monitoring points should be provided at different vertical intervals. Where natural water level variations are likely to exceed 10 m the screened interval may need to be extended.

## A5.4 Annular backfill

### A5.4.1 filter material

The role of a filter material is to support the formation around the screen and, in suitable strata, to provide improved hydraulic characteristics to minimise turbulent flow into a well during pumping. The filter material is typically sand or gravel. It needs to be larger than the effective slot size of the screen, but should not be excessively coarse so that it serves no filtering purpose. For example, the use of 10 mm gravel around screens provides very little filtration potential.

A gravel pack is not an essential design feature for leachate monitoring points, but does have benefits in cushioning the lining from damage and providing a filter between the waste and the screen. Where used, the gravel pack should be larger than the slot size of the lining. For example, a HDPE screen with 3 mm slots could be packed with a 5 or 6 mm single size gravel.

### A5.4.2 Design issues for filter materials

Considerations for filter packs include the following:

* Use a washed, rounded chemically inert sand or gravel (e.g. quartz sand);
* Extend the filter pack to between 0.5 and 2 m above the screened interval to allow for settlement;
* For installations greater than 15 to 20 m deep, particularly below water, use a tremie pipe (e.g. 25 to 50 mm in diameter) to emplace sand to the depth required and avoid bridging on the side walls of the borehole.
* Water may be needed to wash filter material, particularly sand into the borehole. Use only clean water and as little as possible.
* A written record of materials added and depths to the top of each layer should be maintained and recorded with the borehole log and
* A competent person should be on site to supervise and certify the installation.

For more technical details on selection and installation of filter materials, see Aller et al, 1989.

### A5.4.3 Annular seals and grouting

The purpose of annular seals is to isolate the screened section(s) of a monitoring borehole and to prevent contaminants entering the borehole from surface.

Typically, bentonite clay in the form of dehydrated pellets, powder or granules is placed above the filter sand for a depth of at least 1 metre. In some shallow boreholes it may be economic to completely seal to ground surface with bentonite. In deeper boreholes a grout sealant is commonly used. Coated (baked) bentonite pellets can be used to delay the time of hydration of bentonite, and are particularly useful where tremie pipes are used in deeper or multiple installations.

The use of sealants in monitoring boreholes introduces a potential source of contamination, by ‘bleeding’ from the grout or bentonite into the sampling zone. Bentonite can introduce elevated sodium concentrations and fine suspended solids into groundwater. Samples from grout contaminated wells are characterised by high pH values (usually over 10) and elevated magnesium and sulphate (derived from Portland cement). Once contaminated, it can take many years for a grout or bentonite contaminated borehole to lose all traces of contamination.

To reduce this risk, it is recommended that a layer of fine sand be placed above a gravel pack, which should itself extend above the top of screen (after allowing for settlement). Where sand is already used as a screen filter, it may simply be better to extend the height of the sand by a further 0.5m.

Where cement-based grout is used, bentonite pellets should be first added for at least a depth of 1 metre (and preferably for 2 to 3m) above the filter material as a barrier to vertical movement of grout during installation. It is important that the bentonite has hydrated and sealed before adding any grout.

## A5.5 Multi-level monitoring installations

Completion of more than one sampling interval within the same borehole provides a number of challenges for the contractor and competent professional responsible for their design and installation. As interest develops in improving vertical characterisation of contaminant plumes, it is likely that these types of installations will increase in usage. These types of installations should never be installed without competent supervision.

### A5.5.1 Nested installations

The number of nested piezometers than can be placed in one borehole is limited by the borehole size and the size of the tubing (and any couplings) used. Installation, in theory, is similar to that described above for a single piezometer, apart from the need to set separate piezometers into the borehole. There are many practical problems in emplacing more than one structure in a borehole and these should never be attempted without competent supervision. It is recommended that no more than two nested installations should ever be placed in a single borehole. Specific problems are listed below:

* Reducing annulus. As more pipes are added to a borehole the available annulus space reduces. This limits the ability to be able to accurately emplace filter and sealing materials and probably excludes the use of a tremie pipe (see below).
* Settlement. The base of each piezometer in a nested sequence needs to be embedded in filter sand above a sealed layer. Care needs to be taken to avoid each successively higher pipe settling through the underlying sealing layer and
* Excessive pipework. Where multiple pipes are placed in a borehole in which temporary casing has to be removed during installation the risk of jamming or damaging the pipes during removal of temporary casing is heightened.

### A5.5.2 Multi-level installations

Multi-level or multiple-port samplers comprise a modular or continuous single lining string with access ports at specified intervals which allow a hydraulic connection to the adjacent aquifer or sampling zone. There are a number of proprietary systems available for commercial usage. All have common design features.

**Ports with sample tubes**

These types of devices utilise separate access tubes which are attached to ports within a single casing string. The number of ports is determined by how many access tubes can be accommodated within the casing string. Ports are sampled via the access tubes either by using conventional, but narrow diameter, sampling tools or by the use of dedicated gas lift samplers and pressure transducers installed at the ports at the time of construction.

Variants on this system include the following:

* Continuous multi-channel tubing. This is a continuous piece of lining containing pre-formed chambers which removes the need for separate sample tubes and
* “Sock” samplers. The tubes and ports are pre-formed within a continuous porous “sock” prior to installation. The sock is filled with bentonite or other sealant after installation.

**Ports with drained access devices**

These types of devices differ from the above in that ports are fixed within the casing string without tubing access to surface. Each port incorporates a specially designed coupling which locks onto a sampling device lowered into the borehole from surface. Once the sampling device is registered against a specific port, samples are collected by opening the port and gravity-draining water into the sampling device. Level measurements are obtained using transducers located at each port.

### A5.5.3 Sealing and backfilling multilevel installations

**Bedrock installations – use of packers**

Seals between ports on multi-level installations in unweathered and massive bedrock can be formed using packers. Packers are designed to expand into the borehole after installation – either by hydraulic or mechanical inflation from surface, or by natural expansion of material within the packer itself. Some, but not all, packers can be deflated enabling their removal from the boreholes. The use of packers in weathered, highly fractured or poorly competent formations alone is unlikely to provide an effective seal against the borehole sidewall and should be avoided.

Backfill materials can be used above packers to improve sealing.

**Other installations - backfill**

The use of multi-level systems in unconsolidated, fractured or weathered strata requires backfill materials to be placed into the annular space of the borehole. Accurate emplacement of materials is essential and should not be undertaken without competent supervision. In deeper boreholes (e.g. over 20m deep), particularly where materials are placed below the water table, a tremie pipe should be used to ensure materials are placed to the correct depth. The use of fluid sealants (e.g. grout, bentonite mud, synthetic compounds) is not recommended for use where relatively short-screened intervals are sealed between sample ports, due to the inability to properly control the placement and expansion of material to the accuracy required.

**Use of tremie pipes for backfilling**

In using tremie pipes some simple precautions need to be taken:

* Size of tremie pipe. tremie pipe is typically formed from 1 to 3m lengths of flush-threaded plastic pipe. The diameter of the pipe should be sufficient to cope with materials being used – typically they are 25 to 50 mm in diameter. 50mm diameter pipes are preferable. A large funnel should be available to pour materials into the pipe from surface. The tremie pipe should be set no nearer than 1m above the base of the borehole annulus at any time to allow materials to settle freely through the bottom of the pipe into the borehole without clogging up the base of the tremie pipe.
* Filter material. filter material should be used to surround the ports of the multi-level installation which is greater than the slot size of the port, but otherwise as small as possible. For ports with 100 or 250 µm mesh openings, sand of between 0.5 and 1mm in size is adequate. This should be quartz sand.
* Placement of filter material. Sand poured into a tremie pipe will need clean water to be added to avoid blocking the pipe – particularly above water level. A steady but slow flow of water into the tremie pipe works well. The volume of material added should be recorded at all times in order to compare with depth measurements in the borehole. A plumb line should be constantly used to confirm depths. Time should be allowed for sand to settle in the borehole after pouring and before adding further material.
* Sealing material. Where tremie pipes are used it is essential to use a sealing material which will not stick to the sidewalls of the tremie during installation. Coated bentonite pellets are ideal for this use and
* Placement of sealing material. Coated bentonite pellets can be added using the same tremie pipe employed for the addition of filter material. Water is not normally needed as pellets are typically granular and will fall freely under their own weight. The volume of material added should be recorded at all times in order to compare with depth measurements in the borehole. A plumb line should be constantly used to confirm depths. Time should be allowed for the pellets to settle in the borehole after pouring and before adding further material.

## A5.6 Headworks

Headworks should be provided on all completed monitoring points in order to provide safe access for monitoring personnel, unobstructed access for monitoring equipment and to avoid damage from vandalism. The design of headworks will depend on any other uses for the borehole (e.g. gas or leachate extraction).

Headworks can be completed flush with, or protruding above, ground level. Whichever type of completion is selected the completed structure should be sealed into the borehole annulus to prevent surface leakage of water into the borehole. The surrounding area at ground surface should ideally be completed with a concrete pad to shed water away from the borehole and to facilitate sampling.

Protruding headworks are easier to locate and less likely to be effected by surface drainage. Where flush-fitting headworks need to be used (e.g. at sites subject to severe vandalism, or to avoid damage from plant and machinery), borehole logs should incorporate clear descriptions of how to locate these points, particularly in vegetated areas.

## References

Aller, L., Bennett, T.W., Hackett, G., Petty, R.J., Lehr, J.H., Sedoris, H., Nielsen, D.M., and Denne, J.E. (1989). *Handbook of suggested practices for the design and installation of ground-water monitoring wells*. National Water Well Association. USA. Ref: EPA 600/4-89/034 1989.

Barker, J.F., Patrick, G.C., Lemon, L., and Travis, G.M. (1987). *Some biases in sampling multilevel piezometers for volatile organics*. Ground Water Monitoring Review, 7, 2, 48-54.

Baxter, K.M. (1982). *Laboratory leaching experiments using TOC determinations, on low density polythene tubing, polypropylene well casing and a uPVC piezometer tip*. Water Research Centre. Report No. 434-M.

Brandon, T.W. (1986). *Groundwater occurrence, development and protection*. Water Practices Manuals. 5. Institution of Water Engineers and Scientists. ISBN: 0-901427-14-4.

British Standards Institution (1999). Brit*ish Standard BS5930: Code of practice for site investigations*. London.

Driscol, F.G. (1986). *Groundwater and wells*. St Paul, Minnesota, Johnson Division. USA

Dumble, J.P., Charlesworth, D.L., and Haynes, J. (1993). *Groundwater monitoring protocols around landfill sites: The influence of well design, purging methods and sediment on the integrity of groundwater samples*. In: Discharge Your Obligations, 2-4 November 1993, Kenilworth, Warwickshire. edited by Hall, K.E. and Coombs, J., 175-184. CPL Press. Newbury.

Einerson, M.D., Schirmer, M., Pezeshkpour, P., Mackay, D.M., and Wilson, R.D. (1999). *Comparison of eight innovative site characterisation tools used to investigate an MTBE plume as Site 60, Vandenberg Air Force Base, California*. In: NGWA Petroleum Hydrocarbons Conference, 17 Nov 1999-19 Nov 1999, Houston, Texas.

Hutchins, S.R. and Acree, S.D. (2000). *Ground water sampling bias observed in shallow conventional wells*. Ground Water Monitoring Review, Winter 2000, 86-93.

Johnson, T.L. (1983). *A comparison of well nests vs. single-well completions*. Ground Water Monitoring Review, 3, 1, 76-78.

Jones, I., Lerner, D.N., and Baines, O.P. (1999). *Multiport socks samplers: a low cost technology for effective multilevel ground water sampling*. Ground Water Monitoring Review, Winter, 134142.

Pianosi, J.G. and Weaver, T.R. (1991). *Multilevel groundwater assessment of confining units in a bedrock sequence near Sarnia, Ontario*. in: American Institute of Hydrology. Hydrology and Hydrogeology in the'90s. pp. 126-134.

# Appendix 6: Borehole Cleaning and Development

## A6.1 Introduction

Following installation most boreholes require developing in order to remove fluids added during drilling, to clean out silt and clay collected in the borehole and to correct damage caused by the drilling process. The primary objective of borehole development should be to recreate as far as possible the natural conditions surrounding the borehole so that samples which give an appropriate representation of water quality in the surrounding formation can be readily collected.

Borehole development (and cleaning for maintenance purposes) is often an overlooked aspect of monitoring borehole construction, primarily due to the time and cost involved in achieving full development. A balance has to be achieved between the objective of fully developing or cleaning out a borehole and the objective of attaining an appropriate sample of groundwater (or leachate).

The text in the following section is largely paraphrased from Section 7 of Aller et al,

1989, which provides a comprehensive review of monitoring borehole development.

## A6.2 Factors affecting borehole development

Three primary factors influence the process of borehole development:

* Type of geological strata. In hard consolidated rocks such as granites and limestones, few fines are released from the rock matrix so that borehole development can be relatively easily achieved. However, fine materials may form part of the rock matrix, be present in fractures or in weathered sections of the rock.

In consolidated formations such as mudstones, siltstones and fine grained rocks such as chalk, clay and silt particles may be readily freed from the formation into the borehole.

In unconsolidated formations, such as sands, gravels, silts and clays, the structure of the formation immediately around the borehole may have altered during drilling and fine grained particles are readily released from the formation in varying proportions.

* Design and completion of the borehole. In clean, well sorted sands and gravels, monitoring boreholes can be completed relatively easily using an appropriately sized screen with no filter pack.

In fine grained unconsolidated formations, monitoring boreholes are normally completed using a screen and sand filter. Development of these, particularly at depth can be problematical and very slow. Difficulties are compounded where unconsolidated material is stratified and the screened section straddles coarse and fine grained materials.

Filters packs should be at last 50mm thick – i.e. a borehole should be at least 100mm larger than the installed lining and

* Drilling technique. Air rotary rigs will leave fine particles on borehole walls and within fissures adjacent to the borehole. Development procedures should be aimed at removing these fines.

Where casing has been driven or augers used, the interface between the casing and the surrounding formation becomes smeared with fine particulates which must be removed during development.

If drilling fluids, such as mud, are used, the accumulated “mudcake” must be removed during development. Other fluids or additives, which are added during drilling, need also to be removed as efficiently as possible by the development process.

## A6.3 Methods for borehole development

### A6.3.1 Unsuitable methods

The use of air-lift or hydraulic (water or air) jetting techniques should be discouraged within boreholes where these methods have not been used during drilling.

The introduction of air into a monitoring borehole, particularly after installation of the lining, can lead to entrapment of the air in the formation, localised chemical alteration of groundwater, and perhaps most importantly, the destruction of the structure of the formation or filter pack surrounding the borehole screen.

Air used directly from commercial compressors often contains a thin mist of oil. This can be removed from the air stream by the addition of specialist filters or by the use of “oil free” compressors.

Water jetting techniques similarly will result in uncontrolled damage to the filter pack or formation. An exception for the use of water jetting could be made in consolidated rocks where the jetting process may help in loosening fines in fractures and on the side walls of the borehole.

### A6.3.2 Suitable methods

The most suitable methods for borehole development are:

* Bailing.
* surge block or inertial pump surging and
* pumping / overpumping / backwashing.

### A6.3.3 Bailing

**Applications**

Primarily for use in relatively clean, permeable formations.

**Tools**

Weighted bailers with bottom filling valve attached to cable. Can be operated by hand, but a hydraulic winch (typically used with small drilling rig) may be better employed. The bailer should be only slightly smaller in size than the borehole.

**Procedure**

Surge the bailer within the borehole. The most effective operation is where the bail line is allowed to fall rapidly but is then retrieved quickly. This will mobilise finegrained particles from the surrounding formation and in the borehole and lift these into suspension or form a slurry which can then be removed from the borehole by the bailer. Successive bails will remove water and solids from the borehole and induce inflow of particulates through the screen. The procedure should continue until the water is free from suspended particulate matter.

**Problems**

Not effective in fine sand, silts or clays, or in poorly designed boreholes where too vigorous surging action can simply result in increasing volume of fine material being drawn into the borehole. May take a long time.

### A6.3.4 Surge block

**Applications**

To destroy bridging of material and to create sustained agitation needed to develop a borehole. Primarily for use in relatively clean, permeable formations.

**Tools**

1. Drillers surge block used in conjunction with bailer or pump or
2. Large diameter inertial pump (driven mechanically rather than by hand).

**Procedure**

The surge block or inertial pump is moved vertically within the borehole with its position moved along the whole length of the screen. The surging action will mobilise fine-grained particles from the surrounding formation and in the borehole and lift these into suspension or form a slurry. Where an inertial pump is used, fine grained material is continuously pumped from the borehole. Where a surge block is used, this must occasionally be removed from the borehole and a pump or bailer then employed to remove water and particulates, before introducing the surge block again. The procedure should continue until the water is free from suspended particulate matter.

If the borehole is properly designed, increased success with development should be achieved by proceeding along the following steps:

1. Initially operate the surge block with short gentle strokes above the screen intake.
2. Remove particulates regularly (or use an inertial pump).
3. Gradually increase the surging rate at each depth until the particulate concentration reduces and
4. Incrementally increase the depth of surging towards the bottom of the well.

**Problems**

Not effective in fine sand, silts or clays, or in poorly designed boreholes where too vigorous surging action can simply result in increasing volume of fine material being drawn into the borehole.

### A6.3.5 Pumping / overpumping / backwashing

**Applications**

Probably the easiest and most commonly employed technique for well development in any situation.

**Tools**

1. Submersible or similar pump with hose, cable, power source and control equipment or
2. Centrifugal suction pump (where suction is possible – i.e. maximum pumping depth of approximately 8m) and ancillary hose, power source and control equipment or
3. Controlled twin-tube air or fluid lift pump, compressor, rig and ancillary equipment.

**Procedure**

**Pumping** simply involves operating the pump at a yield which is less than or equivalent to the yield of the borehole (i.e. dewatering of the borehole is avoided). This induces groundwater inflow through the borehole screen. Particulates in the flow of water are removed through the pump to surface.

**Overpumping** is where the pump is operated at a capacity greater than the yield of the borehole thereby inducing rapid inflow velocities through the screen which in turn will increase the rate of inflow of particulates. Proper well design is needed to avoid damaging the filter pack in this situation.

**Backwashing** can only be used where a backflow prevention valve is not installed in the pump. The pump is alternatively started and stopped which creates a surging action in the borehole inducing a greater inflow of particulates through the screen into the well which can be then be removed by a sustained period of pumping.

**Problems**

Some risk of damage to the pump, particularly submersibles is involved in this process. Narrow diameter submersible pumps are less able to deal with solids than larger diameter pumps. Overpumping may result in excessive inflow of solids, particularly in silty formations, which could bury the pump.

Use of single high pressure air hoses should be discouraged as these usually result in uncontrolled discharges of grit from the borehole, and may damage the screen and filter pack if these are installed. Limited use of an air hose can sometimes be effective in breaking-up encrusted silt and clay on the base of a borehole where pumping or surging initially fails.

## A6.4 Development in low permeability formations

None of the above methods will be completely satisfactory in low permeability formations. One method proposed by Barcelona et al, 1985 for low permeability consolidated strata (quoted in Aller et al 1989) is as follows.

“Clean water should be circulated down the well casing, out through the well intake and gravel pack, and up the open borehole prior to placement of the grout or seal in the annulus. relatively high water velocities can be maintained, and the mudcake from the borehole wall will be broken down effectively and removed. Flow rates should be controlled to avoid floating the gravel pack out of the borehole. Because of the relatively low hydraulic conductivity of geologic materials outside the well, a negligible amount of water will penetrate the formation being monitored. However, immediately following the procedure, the well sealant should be installed and the well pumped to remove as much of the water used in the development process as possible.”

Other practical advice on development of wells in low permeability formations is provided by Gass, 1986.

## References

Aller, L., Bennett, T.W., Hackett, G., Petty, R.J., Lehr, J.H., Sedoris, H., Nielsen, D.M., and Denne, J.E. (1989). *Handbook of suggested practices for the design and installation of ground-water monitoring wells*. National Water Well Association. USA. Ref: EPA 600/4-89/034 1989.

Barcelona, M.J., Gibb, J.P., Helfrich, J.A., and Garske, E.E. (1985). *Practical guide for groundwater sampling*. Illinois State Water Survey. (SWS Contract Report 327).

Driscol, F.G. (1986). *Groundwater and wells*. St Paul, Minnesota, Johnson Division. USA

Gass, T.E. (1986). *Monitoring well development*. Water Well Journal. 52-55.

Gass, T.E. (1988). *Monitoring well filter pack and screen slot selection*. Water Well Journal. 30-32.

# Appendix 7: Borehole Inspection and Maintenance

## A7.1 Introduction

Most groundwater monitoring boreholes will require periodic maintenance. The most common problem is associated with silt accumulation in the base of a borehole, which can completely block screened intervals. Boreholes may also become blocked due to pinching of the lining or by foreign objects.

Depths can be checked by comparison with details in borehole logs. If borehole logs do not exist, it may be necessary to carry out a caliper, geophysical or camera survey to help identify construction details.

Any boreholes that cannot be rehabilitated should be replaced. In general, abandoned boreholes should be sealed with cement-based grout or bentonite and capped in a manner that prevents any confusion with active monitoring points. The site monitoring plan, drawings and monitoring point register should be amended to clearly document the abandonment.

The text in the following section is drawn from a number of sources, including Appendix B of Blakey et al, 1997 and authors’ experience. A significant part of the text is summarised from Section 8 of Aller et al, 1989.

## A7.2 Factors causing borehole deterioration

### A7.2.1 Poor borehole design

Boreholes constructed with inappropriately sized well screens and filters are likely to cause long term maintenance problems. Other problems may arise from the use of filter materials which are chemically incompatible with the groundwater or leachate or by the use of poor quality borehole linings which may collapse due to hydrostatic pressures.

### A7.2.2 Poor installation technique

If records recording the installation process are not available, and particularly if a competent person was not present on site to take responsibility for quality assurance, questions can reasonably be raised on the integrity of the borehole construction. Borehole screens may be inappropriately positioned, filter material may be inaccurately placed, bentonite or cement seals may be poorly prepared and badly placed and may even bridge the screened interval where it may contaminate water samples. Surface water may enter poorly sealed boreholes through the annular space.

### A7.2.3 Poor development

The aims of developing a borehole after construction is to remove materials and effects arising from the drilling process (See Appendix 6) as well as to remove fines from the filter pack, borehole and formation. Lack of development can compromise water quality and in some cases can lead to clogging of the borehole with drilling muds.

### A7.2.4 Borehole stability

Unstable boreholes can arise from the use of thin-walled linings which are incapable of resisting hydrostatic pressures or waste movement, and improper screen placement combined with excessive pumping resulting in screen collapse.

### A7.2.5 Incrustation

Incrustations on well screens or within filter material arise as three types:

* Chemical. Typically caused by carbonate, hydroxide or sulphate precipitation on or within the screen intake.
* Physical. Typically caused by sediments plugging the intake or surrounding filter or strata and
* Biological. Typically caused by bacteria growing in the filter, or surrounding formation, or within the borehole. Bacterial growth is dependent on the quantity of nutrients present which may be contained within the formation water or may have been introduced by the drilling process. The type of bacteria is dependent on the absence or presence of oxygen. Bacterial growth is very common in leachate wells – often resulting in “foaming” on the leachate surface and slime coatings on the side of boreholes – particularly in boreholes which are regularly pumped.

Incrustation problems are commonly caused by a combination of the above processes.

## A7.3 Checks on borehole performance

Periodic checks on the performance of a monitoring borehole can be introduced routinely into monitoring programmes and should be carefully documented. Performance data should be periodically reviewed to ensure samples and water level measurements are not unduly influenced by deterioration of the borehole. Specific checks on performance include the following:

* Borehole depth measurement. Depth measurements should be recorded at least annually and, if possible, every time a sample is taken.

Depth measurements should be compared with the original depth recorded on borehole logs and with the depth of the screen interval in the borehole. If the screened section of the borehole is blocked (e.g. with sediment) the validity of data from the borehole may be called into question.

* Water level variations. Maximum and minimum water levels should be reviewed (annually or two-yearly) with comparison to the level of the top of the screen intake.

If the water level in the borehole falls below the top of the screen intake, then samples taken from the borehole can alter compared to samples collected when the water level lies above the screen intake. For boreholes where this is a regular occurrence (e.g. those used for combined gas and groundwater monitoring), the variation in chemistry caused by this effect would become part of the natural variability recorded during the initial characterisation monitoring programme and ongoing baseline. For boreholes where this happens rarely, a change in water level below the screen intake may help explain anomalous data.

* Comparative water level data. Water level measurements from all boreholes should be routinely compared against other boreholes in the same groundwater system.

Water levels expressed in metres above Ordnance Datum (m.AOD) should be plotted in time-series format against other boreholes in the same groundwater system, or against other boreholes in the same hydraulic landfill cell. Where there are marked departures in trends between boreholes (which have been validated by remeasurement) this may be due to poor design of the borehole or some deterioration in the borehole structure.

Care should be taken in comparing data from boreholes in the same landfill cell, particularly in well-compacted and deep landfills. Perched water levels are commonly developed, which may result in completely different water level variations which cannot be used for this purpose.

* Reduction in borehole yield. Drawdown levels during pumping of boreholes should be routinely recorded and reviewed periodically.

Where boreholes are pumped, particularly throughout a prolonged period of purging, the water level should be recorded before and after pumping. Comparison of the maximum drawdown achieved for a particular pumping rate and how this changes with time will provide an indicator of whether or not the yield of the borehole is declining. If the drawdown in water level increases for the same pumping rate, then it is possible that some blockage is occurring around the well screen or within the adjacent formation.

Where drawdown data has not been recorded routinely during sampling, hydraulic conductivity tests could be used as a more formal alternative for comparing the hydraulic efficiency of a borehole.

In all cases, care should be taken when interpreting data from boreholes in which the water level lies within the screened interval. A change in water level may result in completely different yield characteristics due to vertical variations in the natural permeability of the adjacent strata and

* Increased sediment loading of samples. A descriptive note of sediment loading in a sample should be maintained as part of routine record keeping during sampling.

In poorly designed or undeveloped monitoring boreholes, sediment input to the borehole may increase with time. If sediment loading is persistent or noticeably worsens with time, then this may influence the quality of the water samples and / or lead to sediment accumulation in the borehole (which will be revealed by depth measurements).

## A7.4 Investigative techniques

### A7.4.1 Introduction

In situations where a borehole design is unknown or an obstruction or constriction has been identified, down-hole investigations may be undertaken to try and provide a clearer picture of the borehole structure or blockage. Some geophysical methods may also provide information which can be used to interpret conditions in the strata around the borehole or in the annulus.

A summary of geophysical logs, their application, and requirements are shown in

Table A7.1 which, along with the following summary of methods is extracted from Blakey et al 1997. Not all techniques are appropriate to all boreholes and specialist advice should be taken before any one method is used. In general, a combination of logs is necessary to allow reliable interpretation of results. Interpretation of data, particularly geophysical data, can be ambiguous and should not be attempted without specialist knowledge of the limitations and applicability of the technique.

Some of the logs only operate in water while others can only be used in uncased boreholes. The requirements are given in Table A7.1.

Most of the tools have a diameter of 50 mm or less. The upper diameter limit for geophysical logging varies according to the tool being used. The formation logs, resistivity, spontaneous potential and natural gamma start to lose definition at diameters above about 300 mm, while temperature and heat pulse flow meter logs may be distorted by convective flow in large diameter boreholes.

The most frequently used downhole logging techniques are described below.

**Table A7.1: Comparison of downhole logging techniques**

| **Log** | **Borehole Fluid** | **Casing** | **Borehole construction** | **Lithology** | **Fractures** | **Fluid movement** | **Fluid quality** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Resistivity | Required | Uncased or plastic screen | - | Y |  | - | Y |
| Spontaneous Potential | Required | Uncased or plastic screen | - | Y | - | - | Y |
| Natural Gamma | Not Required | Cased or Uncased | Y | Y | - | - | - |
| Gammagamma | Not Required | Cased or Uncased | - | Y | - | - | - |
| Neutron | Not Required | Cased or Uncased | - | Y | - | - | - |
| Sonic | Required | Uncased | Y1 | - | Y | - | - |
| Caliper | Not Required | Cased or Uncased | Y | - | Y | - | - |
| Temperature | Required | Cased or Uncased | - | - | - | Y | - |
| Conductivity | Required | Cased or Uncased | - | - | - | - | Y |
| Flowmeter | Required | Cased or Uncased | - | - | - | Y | - |
| Television | Not Required  Must be clean | Cased or Uncased | Y | - | Y |  | - |

1 Can be used in cased hole to check cement grout.

### A7.4.2 Physical logs

* CCTV or other cameras. A closed circuit television (CCTV) inspection of a lined borehole is probably the most effective means of identifying screen position or damage such as clogged screens or blockage. Cameras need to be selected carefully in relation to the diameter of the boreholes being investigated. In turbid waters, picture resolution may be poor.
* Caliper log. This tool has three spring-loaded arms which measure the diameter of the borehole. It can indicate probable fracture zones in unlined boreholes and may be used to confirm the diameter of an unlined borehole. The spring-loaded arms may catch and damage borehole screens and should only be used for screen identification after exhausting all other methods.

### A7.4.3 Formation logs suitable for use in lined boreholes

* Natural gamma log. The natural gamma log is a measure of the natural gamma radiation emitted from the formation. It is usually assumed that the natural gamma radiation is caused by the decay of potassium-40 and therefore a high gamma count is interpreted as a high potassium-bearing formation such as clay or shale. Limestone will normally have a low gamma count and sandstone an intermediate count.

This is the most useful of the lithological logs as it can be used in both the saturated and unsaturated zones. It is most commonly carried out prior to installation of a monitoring borehole lining. Since gamma radiation passes through casing, a useful log can be obtained within temporary steel casing or within a lined monitoring borehole.

Gamma logs will react to cement grout or bentonite behind a borehole lining and, depending on the contrast against the natural formation, may provide an indication of the integrity of borehole construction.

### A7.4.4 Other formation logs for use in open boreholes

The following logs are used normally for site investigation purposes within unlined boreholes and have no specific application in lined monitoring boreholes:

* Gamma-gamma (Density). The gamma-gamma or density log is the result of lowering a collimated gamma source into the borehole. The gamma radiation is directed into the formation and is attenuated according to the formation properties. It is most attenuated by high atomic weight elements, so a non-porous rock with high calcium, magnesium and iron concentrations will have more effect than a highly porous rock with lighter elements (and pore spaces containing hydrogen in the form of water). It is a difficult log to run as it requires a smooth borehole wall to ensure that the gamma radiation is directed into the formation and not into the borehole.
* Neutron (Porosity). The neutron log is similar in its operation to the density log. In this case it is a source of neutron radiation which is lowered into the borehole and the reaction between neutrons and hydrogen atoms which is recorded. The number of hydrogen atoms will, in most cases, be proportional to the porosity of the formation and hence the resulting log can be interpreted in terms of porosity. Like the density log, this log is most effective in a uniform, small diameter borehole. In theory it can be run in a steel-cased borehole, but since it is affected by diameter changes behind the casing, interpretation can be ambiguous. Plastic casing contains a high proportion of hydrogen atoms and will have a marked effect on the log.
* Resistivity log. Resistivity logs cannot be used in cased boreholes or above the water table. Plastic casing is non-conducting and electrical current will not be able to pass into the formation, while steel screen will cause a short circuit between the electrodes.

This is a measure of the resistivity of the formation. Various methods of measurement are available such as single point, 16 and 64 inch normal, guard and laterolog, the difference being the distribution and spacing of the electrodes. The measurement made is mainly of the resistivity of the formation porewater. In fresh water aquifers, high resistivity indicates that the formation has low porosity, such as limestone or crystalline rocks. Low resistivity indicates high porosity formations such as unconsolidated clay, sand or gravel. However highly conductive water such as found in cases of saline intrusion and leachate contamination may give a similar reported effect. Experienced personnel are required for good interpretation of logs where conditions are difficult.

* Spontaneous potential logs. Spontaneous potential logs cannot be used in cased boreholes or above the water table. Plastic casing is non-conducting and electrical current will not be able to pass into the formation, while steel screen will cause a short circuit between the electrodes.

This is a measurement of the natural electrical potential which is developed when the salinity of the borehole water differs from the porewater in the formation. Its main use is in boreholes drilled with a saline mud (a practice which is normally discouraged in landfill investigations). However, it might detect zones of leachate within an aquifer containing mostly fresh water and

* Sonic. This tool propagates sound waves into the formation and records their characteristics in terms of fracturing and hence permeability. If used successfully, the permeable horizons in the borehole can be delineated and these will show the main flow horizons in the aquifer.

### A7.4.5 Fluid logs

Fluid logs can be readily run in lined or unlined boreholes to investigate vertical variation in water properties, which in turn may reveal information on movement of water into and out of the borehole. These are particularly useful in boreholes with very long screens or where groundwater flow is stratified or where fissure flow is dominant:

* Temperature. This is a log of the borehole fluid temperature. Where no vertical flow occurs in an aquifer, the groundwater temperature steadily increases with depth at the rate of about 2°C per 100 m. Departures from this gradient in a borehole can mean that a vertical fluid flow is occurring in the borehole; distinct steps in the temperature profile usually indicate inflow levels. The temperature regime in the vicinity of landfills is modified by heat generated by the decomposition process within the landfill itself, and temperature anomalies in the borehole log can indicate that the water is polluted by the landfill.
* Conductivity. The electrical conductivity of the borehole fluid is proportional to the dissolved solids and hence groundwater quality. A conductivity log will therefore indicate polluted zones within the borehole, but the interpretation needs to take account of any vertical flow which may be taking place within the borehole and
* Flowmeter. A spinner flowmeter will not normally be sufficiently sensitive to measure naturally occurring vertical flows in the borehole. A more sensitive type, such as the heat pulse flowmeter, will be more suitable. This can measure flow rates down to 1 mm/s and will operate in a 50 mm diameter borehole. Convective flow may develop in boreholes with diameters larger than about 300 mm and this will interfere with heat pulse flowmeter measurements.

## A7.5 Maintenance and rehabilitation of boreholes

### A7.5.1 Sediment removal

The most common maintenance problems are the accumulation of sediment at the bottom of the borehole or the need to recover foreign objects (rocks, insects, vegetation etc) dropped into the borehole.

Options for removing sediment from a borehole are limited and include the following:

* Boreholes less than 8m deep (within suction lift depth). Use a centrifugal pump and place the intake in the sediment at the base of the borehole, which should “vacuum” lift the sediment. Water is needed to fluidise the sediment and may need to be added.
* Boreholes up to 60m deep. Use an inertial pump and surge this into the sediment at the base of the well. Once fluidised, sediment can sometimes be lifted through the pump to surface. If sediment blocks the hole above water level, water may need to be added from surface to fluidise it.
* Boreholes any depth. Use a bailer, which where used with a winch (e.g. on a small drilling rig), can be effective.

Use of single high pressure air hoses should be discouraged as these usually result in uncontrolled discharges of grit from the borehole, and may damage the screen and filter pack. Limited use of an air hose can sometimes be effective in breaking-up encrusted silt and clay on the base of a borehole where pumping or surging initially fails. Controlled twin-tube air or fluid lift pumps can be used to pump sediment.

### A7.5.2 Chemical treatment

Chemical treatment (often combined with mechanical techniques) has been traditionally used to restore well yields in production boreholes. These techniques are not commonly used for monitoring boreholes since the addition of chemicals can cause severe changes in the borehole environment which may be long lasting or even permanent. These changes may adversely effect some or all future water quality samples. If chemical agents are introduced, analysis of the borehole water immediately before and after treatment should be undertaken to provide a measure of the impact of the treatment.

Three categories of chemicals are used:

* Acids. Primarily used to dissolve incrustations.
* Biocides. Primarily used to kill bacteria and
* Surfactants. Primarily used to disperse clay by lowering the surface tension of the water.

### A7.5.3 Mechanical rehabilitation

Mechanical rehabilitation methods to improve well yield are the same methods used for well development (see Appendix 6). The uncontrolled use of high-pressure air should be discouraged.

Any type of rehabilitation for incrustation can be supplemented by the use of a wire brush or mechanical scraper alongside bailing or pumping to remove loose particles on the side walls of the screen or borehole. Blockages can sometimes be dealt with using drain rods.

### A7.5.4 External borehole maintenance

Routine inspection and maintenance of the exposed section of borehole and protective headworks should include the following:

* Surface seal / concrete pad. Any cracks or damage to the surface seal surrounding the borehole and headworks should be repaired in order to prevent surface water entry to the borehole surrounds. In cases of extreme damage, the entire seal should be broken out and replaced.
* Protective headworks. Protective headworks should be maintained so that they are kept free of rust, allow ready access by monitoring personnel, and protect the borehole from vandalism and ingress of water and foreign objects. Locks should be maintained in operational condition.
* Borehole lining cover. A cover should be maintained separately on top of the borehole lining to prevent foreign objects accidentally falling into the borehole. Where sampling devices or tubes extend beyond the top of a borehole lining, these should be checked for blockages and purpose designed lining caps should be provided to avoid foreign objects accidentally falling into the borehole and
* Labelling. External and internal labelling should be maintained in good condition and should correspond exactly with the monitoring point register. Particular care is required in the maintenance of labelling on multiple monitoring points.

## References

Aller, L., Bennett, T.W., Hackett, G., Petty, R.J., Lehr, J.H., Sedoris, H., Nielsen, D.M., and Denne, J.E. (1989). *Handbook of suggested practices for the design and installation of ground-water monitoring wells*. National Water Well Association. USA. Ref: EPA 600/4-89/034 1989.

British Standards Institution (1999). *British Standard BS5930: Code of practice for site investigations*. London.

Driscol, F.G. (1986). *Groundwater and wells*. St Paul, Minnesota, Johnson Division. USA Environment Agency: National Groundwater and Contaminated Land Centre (1998). *Decommissioning redundant boreholes and wells*. Environment Agency.

# Appendix 8: Example Monitoring Record Forms

## A8.1 Introduction

A number of example forms are provided in this appendix for recording monitoring data:

* Table A8.1 Environmental observations.
* Table A8.2 Water movements.
* Table A8.3 Equipment calibration.
* Table A8.4 Water levels.
* Table A8.5 Borehole purging and field measurements.
* Table A8.6 Sample collection and
* Table A8.7 Chain of custody.

## A8.2 Environmental observation record form

An example form is provided as Table A8.1. This form could be adapted as part of a general site diary covering environmental observations. Descriptions of information and examples applicable to each heading follow:

**Table A8.1a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for individual monitoring point. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| Date From | Start of recording period | 1 January 2001 |
| Date To | End of recording period | 31 January 2001 |

**Table A8.1b: Data requirements**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Date | Date of observation | 5 January 2001 |
| Type of Observation | Category of observation | RO Run-off to stream  Veg Vegetation die-back  Lch Leachate seepages |
| Location of observation | Description of observation location.  Use local names, or grid reference as appropriate. Could be used in conjunction with plan of site with observational points indexed by number. | Northern edge of cell 1.  Northern site ditch (Grid  Reference: SP 12345 67890) Land off-site adjacent to western site boundary |
| Details | Brief description of observation | Leachate seepages at surface Suspended solids entering ditch following heavy rainfall. Gaps in crop growth adjacent to site boundary – gas damage? |
| Action Taken | Brief note of follow-up action taken (if any) | Referred to Technical Manager Known problem – ongoing monitoring in hand  Interceptor ditch constructed on (date). |
| Recorded by | Name of person recording observation | A. Smith |
| Notes | Any other general notes relevant to observations | Exceptional heavy rainfall between 1 and 5 January Transferred main landfill input from Area A to Area B during  January. |

**Table A8.1c: Quality assurance**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Name | Name of person responsible for supervising or managing work. | Survey Person responsible for taking field measurements  QC Manager Person responsible for QC checks of data  Manager Person responsible for monitoring programmes |
| Date | Date when each task, including paperwork is completed. | 3/3/00 |
| Inits. | Initials of responsible person. | ABC |

**Table A8.1d: Data processing trail**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Schedule Completed | Date confirming schedule has been checked against Monitoring Plan Specification and signed off as completed.  Include initials of person responsible for planning survey work. | 10/3/00, ABK |
| Data Validated | Date when data has been double-checked and validated.  Include initials of person responsible for validation. | 15/3/00, PDW |
| Computer Updated | Date when data has been entered into computer system (where used).  Include initials of person responsible for data entry. | 15/3/00, PDW |

**Table A8.1e: Example field sheet for environmental observations**

**Table A8.1e(a) Environmental Observation Record Form**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Date From** |  |
| **Date To** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.1e(b): Record Form**

| **Date** | **Type of Observation** | **Location of Observation (include Grid Reference if a specific point of observation)** | **Details** | **Action Taken** | **Recorded By** |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |

**Table A8.1e(c): Quality Assurance and Data Processing Trail**

|  |  |  |  |
| --- | --- | --- | --- |
|  | **Name** | **Date** | **Inits** |
| **Quality Assurance – Record Checked** |  |  |  |
| **Quality Assurance – QC Manager** |  |  |  |
| **Quality Assurance – Manager** |  |  |  |
| **Data Processing Trail – Schedule Completed** |  |  |  |
| **Data Processing Trail – Data Validated** |  |  |  |
| **Data Processing Trail – Computer Updated** |  |  |  |

## A8.2 Water movements record form

An example form is provided as Table A8.2. This form is a summary of information over a specified period and would draw information from a number of different sources at a landfill. Any removal or addition of water should be included in the record.

The form does not include all information necessary to analyse the water balance for a specific part of a site but is intended to include all relevant water measurements that can be usefully recorded from which a water balance could be constructed. Other data such as waste type, waste volume, waste density, waste absorption, cell geometry, restoration cover, infiltration etc are necessary to fully evaluate a water balance.

**Table A8.2a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| Total Rainfall  During Period  (mm) | Total rainfall in mm recorded from site records or from Met Office data. | 25 |
| Period of Summary | Start and end date for summarised data.  An annual summary should be prepared as a minimum. | 1 to 31 January 2002  1 January to 31 March 2003  1 Jan to 31 Dec 2003 |
| Date Prepared | Date summary sheet prepared. | 31 January 2001 |

**Table A8.2b: Data requirements**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Site Area Name | Site Area or Landfill Cell Name  Separate details should be provided for each hydraulically separate landfill cell in which water other than rainfall has been artificially removed or applied. | Cell 1 |
| Percent Capped | Estimate of the average percentage of site area that was covered with a low permeability capping layer during recording period. | 0%, 100%, 25% |
| Effective Rainfall | Rainfall in mm falling onto site area after accounting for evapotranspiration losses.  Leave blank if not known. | 10 |
| Leachate Transfers In. | Total volume of liquid removed from other parts of the site and disposed into this site area (m3). | 540 |
| Transfer Source | Area from which transfer originated | Cell 2 |
| Other Inputs | Total volume of liquids disposed from other external sources - in m3.  For example, clean water (e.g. added to enhance biodegradation). | 90 |
| Discharges Off-site | Total volume of liquid removed and disposed off-site - in m3.  For example, to sewer or via tanker to treatment works. | 360 |
| Leachate Transfers Out | Total volume of liquid removed and transferred for disposal to other parts of site - in m3.  If disposed to more than one other area, itemise each separately. | 480 |
| Transfer Destination | Area to which transfer was made | Cell 3 |
| Other Outputs | Total volume of liquids removed by any other means -in m3. | 13 |
| Leachate Level Change | Average recorded change in leachate level over period based on monitoring results - in m. | +0.4, -0.2, 0.0 |
| Comments | Any notable points. | Sharp rise in leachate levels probably caused by recent overfilling of older wastes.  Leachate volume estimates are based on pump usage time – significant uncertainty. |
| Totals | Sum of each unshaded column.  Total leachate transfers recorded as inputs and outputs should be equal. | - |

**Table A8.2c: Quality assurance**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Name | Name of person responsible for supervising or managing work. | Record Checked: Person responsible for collating data  QC Manager: Person responsible for QC checks of data  Manager: Person responsible for monitoring programmes |
| Date | Date when each task, including paperwork is completed. | 3/3/00 |
| Inits. | Initials of responsible person. | ABC |

**Table A8.2d: Data processing trail**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Schedule Completed | Date confirming when schedule has been checked against Monitoring Plan Specification and signed off as completed.  Include initials of person responsible for planning survey work | 10/3/00, ABK |
| Data Validated | Date when data has been double-checked and validated.  Include initials of person responsible for validation. | 15/3/00, PDW |
| Computer Updated | Date when data has been entered into computer system (where used).  Include initials of person responsible for data entry. | 15/3/00, PDW |

**Table A8.2e: Example field sheet for recording water movements**

**Table A8.2e(a): Water Movements Record Form**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Total Rainfall During Period (mm0** |  |
| **Period of Summary (From/To)** |  |
| **Date Prepared** |  |
| **Summary Prepared by** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.2e(b): Record Form**

| **Site Area Name** | **Percent Capped**  **%** | **Effective Rainfall**  **mm** | **Leachate Transfers In**  **mm3** | **Transfer Source** | **Other Inputs**  **m3** | **Discharges off-site**  **m3** | **Leachate Transfers Out**  **m3** | **Transfer Destination** | **Other Outputs**  **m3** | **Leachate Level Change**  **m** | **Comments** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |

**Table A8.2e(c): Quality Assurance and Data Processing Trail**

|  |  |  |  |
| --- | --- | --- | --- |
|  | **Name** | **Date** | **Inits** |
| **Quality Assurance – Record Checked** |  |  |  |
| **Quality Assurance – QC Manager** |  |  |  |
| **Quality Assurance – Manager** |  |  |  |
| **Data Processing Trail – Schedule Completed** |  |  |  |
| **Data Processing Trail – Data Validated** |  |  |  |
| **Data Processing Trail – Archive Records Updated** |  |  |  |

## A8.3 Equipment calibration forms

An example form is provided as Table A8.3. This form covers field instrumentation in common usage but may need to be modified to cover other instrumentation.

**Table A8.3a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| Survey Reference | Survey Title | Quarterly Survey – May 2001  Six-Monthly Survey – June 2001. |
| Survey Personnel | Name(s) of survey personnel  Include company name if work undertaken by external contractor | AB Smith (AA Monitoring Co) |

**Table A8.3b: Water level dip meters**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Date | Date of calibration check | 26 June 2001 |
| Field Instrument - Model /Serial Number | Model and serial number of dip meter | ABC Co Supreme Dipmeter, AB1234567 |
| Field Instrument - Total Length | Total length of dip meter in metres | 60.000 |
| Field Instrument - Dip Meter Measurement Against Standard | Length of standard tape length measured with dip meter (metres) | 60.005 |
| Standard – Describe | Description of standard tape used | ABC Tools certified metal tape |
| Standard – Tape Length | Length of tape used to check against dipper (metres) | 100.000 |
| Difference | Difference in length between two tapes (Dip Meter Measurement – Standard Tape Length) – metres | 0.005 |
| Initials | Initials of person carrying out measurement. | PBC |

**Table A8.3c: Water quality instruments used in survey**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Inst No | Reference Number used in calibration table to identify instrument | 1, 2, 3 |
| Type | Type of instrument | Temp, pH, EC, DO, Eh. |
| Units of measurement | Units used for calibration | deg C, pH units, µS/cm, % saturation, mV. |
| Model | Model name for instrument | OK Equipment Co, AB-300 |
| Serial No | Serial number of instrument | AKW-347819 |
| Comments | Any relevant comments | New probe recently purchased |

**Table A8.3d: Calibration records**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Inst No | Reference Number used in calibration table to identify instrument | 1, 2, 3 |
| Date | Date of calibration | 23 / 7 / 01 |
| Time | Time of calibration | 09:05 |
| Calibration Standard 1 (&2) | Standards for calibration | see below |
| Ref Std 1 (&2) | Measurement value of standard solution in appropriate units.  For pH meters these are the buffer standards. | EC Meters 1000µS/cm pH Meters 4.01, 7.01, 10.01 DO Meters Zero% oxygen |
| Reading Before Cal | Reading by instrument immediately before calibration.  Indicates drift from previous reference for instruments calibrated more than once during survey – For example, pH meters. | 6.97 (against standard of 7.01) |
| Cal (√) | Tick after calibrating to standard | √ |
| Inits | Initials of person carrying out calibration | PBC |

**Table A8.3e: Quality assurance**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Name | Name of person responsible for supervising or managing work. | Survey Person responsible for taking field measurements  QC Manager Person responsible for QC checks of data  Manager Person responsible for monitoring programmes |
| Date | Date when each task, including paperwork is completed. | 3/3/00 |
| Inits. | Initials of responsible person. | ABC |

**Table A8.3f: Example field sheet for recording equipment calibration**

**Table A8.3f(a): Equipment Calibration Record Form**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Survey Reference** |  |
| **Survey Personnel** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.3f(b): Water Level Dip Meters**

| **Date** | **Field Instrument**  **Model / Serial Number** | **Field Instrument**  **Total Length**  **m** | **Field Instrument**  **Dip Meter Measurement Against Standard**  **m** | **Standard**  **Describe** | **Standard**  **Tape Length**  **m** | **Difference**  **m** | **Initials** |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |

**Table A8.3f(c): Water Level Dip Meters - Comments**

| **Comments (Note: If difference is greater than 1cm over 30m then dip meter should be replaced)** |
| --- |
|  |

**Table A8.3f(d): Water Quality Instruments Used in Survey**

| **Inst No** | **Type** | **Units of Measurement** | **Model** | **Serial No** | **Comments** |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |

**Table A8.3f(e): Calibration Records**

| **Inst No** | **Date** | **Time** | **Calibration Standard 1**  **Ref Std 1** | **Calibration Standard 1**  **Reading Before Cal** | **Calibration Standard 1**  **Cal**  **(√)** | **Calibration Standard 2**  **Ref Std 2** | **Calibration Standard 2**  **Reading Before Cal** | **Calibration Standard 2**  **Cal**  **(√)** | **Initials** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |

**Table A8.3f(f): Calibration Records - Comments**

| **Comments** |
| --- |
|  |

**Table A8.3f(g): Notes**

| **Notes** |
| --- |
|  |

**Table A8.3f(h) – Quality Assurance**

|  | **Name** | **Date** | **Inits** |
| --- | --- | --- | --- |
| **Survey** |  |  |  |
| **QC Manager** |  |  |  |
| **Manager** |  |  |  |

## A8.4 Water level record form

An example form is provided as Table A8.4. This form could be used or modified for use for recording groundwater levels, leachate levels or surface water levels when these are being measured without sampling. Descriptions of information and examples applicable to each heading follow.

**Table A8.4a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| Survey | Survey Title | Monthly Survey – May 2001  Quarterly Survey – June 2001. |
| Survey Personnel | Name(s) of survey personnel  Include company name if work undertaken by external contractor | AB Smith (AA Monitoring Co) |

**Table A8.4b: Data requirements**

All monitoring points scheduled for monitoring should be included on this form. An explanatory comment should be provided where no data is obtained. This will facilitate with comparison against schedules set out in the Site Monitoring Plan.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Date | Date of measurement | 3/7/2001 |
| Time | Time of measurement (Not always necessary). | 14:50 |
| Mon Point | Monitoring point reference number | GW1, L1 |
| Datum  Description | Simple description of datum point used for water level measurements. | Top of external casing  Top of internal lining  Yellow mark on bridge deck |
| Datum Elevation | Surveyed elevation of datum point.  Expressed as metres above Ordnance Datum. | 95.42 |
| Datum Status | Code indicating reliability of datum elevation. | S Surveyed  E Estimated  U Unknown |
| Depth to Water | Depth to water level  Recorded as metres below datum point (m.b.d)  If dry record as “dry”. | 3.56 |
| Depth to Base | Depth to base of monitoring point  Recorded as metres below datum point (m.b.d). The depth should be measured if the monitoring point is dry or if the datum point has changed. Otherwise it should be recorded at least annually. | 3.56 |
| Comments | Record any relevant information which may influence water levels measurements. | Base silted-up since last survey  Datum raised since last survey  - new concrete rings added  Headworks damaged – in need of repair  Flooding around headworks |
| QC | Data checked by QC supervisor for obvious errors in field data | Highlight records which are anomalous.  Tick records which are consistent with historic data. |
| Notes | Other additional information  For example, unusual weather, access or safety problems requiring attention. | Torrential rain overnight Damaged headworks. |

**Table A8.4c: Quality Assurance**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Name | Name of person responsible for supervising or managing work. | Survey Person responsible for taking field measurements  QC Manager Person responsible for QC checks of data  Manager Person responsible for monitoring programmes |
| Date | Date when each task, including paperwork is completed. | 3/3/00 |
| Inits. | Initials of responsible person. | ABC |

**Table A8.4d: Data processing trail**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Schedule Completed | Date confirming when schedule has been checked against Monitoring Plan Specification and signed off as completed.  Include initials of person responsible for planning survey work. | 10/3/00, ABK |
| Data Validated | Date when data has been double-checked and validated.  Include initials of person responsible for validation. | 15/3/00, PDW |
| Computer Updated | Date when data has been entered into computer system (where used).  Include initials of person responsible for data entry. | 15/3/00, PDW |

**Table A8.4e: Example field sheet for recording water levels only**

**Table A8.4e(a): Water Level Record Form**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Survey Reference** |  |
| **Survey Personnel** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.4e(b): Water Level Record Form**

| **Date** | **Time** | **Mon Point** | **Datum Description** | **Datum Elevation**  **m.AOD** | **Datum Status**  **S / E / U** | **Depth to Water1**  **m.b.d** | **Depth to Base2**  **m.b.d** | **Comments** | **QC** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |

1 If monitoring point is dry, record as “dry”.

2 Depth to base should always be measured if monitoring point is dry.

**Table A8.4e(f): Notes**

| **Notes** |
| --- |
|  |

**Table A8.4e(g) – Quality Assurance and Data Processing Trail**

|  | **Name** | **Date** | **Inits** |
| --- | --- | --- | --- |
| **Quality Assurance: Survey** |  |  |  |
| **Quality Assurance: QC Manager** |  |  |  |
| **Quality Assurance: Manager** |  |  |  |
| **Data Processing Trail: Schedule Completed** |  |  |  |
| **Data Processing Trail: Data Validated** |  |  |  |
| **Data Processing Trail: Computer Updated** |  |  |  |

## A8.5 Borehole purging record

An example form is provided as Table A8.5. This form could be used to record purging from any vertical structure. Once purging strategies have been established for monitoring points, this form can be condensed to record the information appropriate for the strategies used. It may then be combined with the sample collection form (A.8.6 below).

**Table A8.5a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| Weather Conditions | Weather conditions on day of survey | Overcast and cloudy and cool following week of heavy rainfall. |
| Survey Reference | Survey Title | Quarterly Survey – June 2001  Six-Monthly Survey – September 2001 |
| Survey Personnel | Name(s) of survey personnel  Include company name if work undertaken by external contractor | AB Smith (AA Monitoring Co) |
| Monitoring Point | Monitoring point reference number | GW1, L1 |

**Table A8.5b: Strategy and equipment used**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Purge Strategy | Purging method adopted | SWQ Pump until WQ determinands stabilise  3xBV Pump 3 x well volumes  D&R Dewater hole and allow water level to recover LFT  Low flow timed purge (rate and time based on prior testing)  LFP Low flow purging using dedicated pump  DS Depth sample – no purging  SS Surface sample – no purging |
| Purge equipment | Type of equipment used for purging | Bailer  Inertial pump  Submersible  Bladder Pump |
| Dedicated pump | Y – Yes if installed at least 24 hours in advance of purging. N - No otherwise. | Y |
| Flow Measurement | Method for recording flow and / or purge volume | Bucket with stopwatch Flow meter |

**Table A8.5c: Monitoring point measurements and well volume estimate**

All monitoring points scheduled for monitoring should be included on this form. An explanatory comment should be provided where no data is obtained. This will facilitate with comparison against schedules set out in the Site Monitoring Plan.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Date of measurement | Date of purging | 3 / 7 / 2001. |
| Liner ID | Internal diameter of borehole lining in mm | 50 |
| Datum point | Brief description of datum point used for water level measurements | Steel cap  Top of internal liner |
| Depth to Water | Depth to water level.  Recorded as metres below datum point (mbd). If dry record as “dry”. | 3.56  Dry |
| Depth to Base | Depth to base of monitoring point  Recorded as metres below datum point (mbd). The depth should always be measured if the monitoring point is dry. | 5.67 |
| Depth of water | Depth of water above base of borehole lining.  Difference in value between “Depth to Base” and “Depth to Water”. | 2.11 |
| Well volume | Volume in litres  Calculated from equation V = 1000.π.  (D/2000)2.h (where π = 3.142, D = diameter of borehole lining in mm and h is saturated depth in m). | For a 50mm diameter well with a saturated depth of 2.11m: V = 1000 x 3.142 x (50 /  2000)2 x 2.11 = 4.1 litres |
| 3 x well volume | 3 times well volume in litres.  Only needed if purge strategy is to remove 3x well volumes. | 4.1 x 3 = 12.3 litres |

**Table A8.5d: Purging record**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Start time of purging | Time pumping commenced (only needed for timed purge). | 14:50 |
| End time of purging | Time pumping ceased (only needed for timed purge). | 14:58 |
| Purge duration | Difference between end time and start time expressed in minutes (only needed for timed purge). | 14:58 – 14:50 = 8mins |
| Purging rate | Average rate of purging if measured  Only needed for timed purge. Alternatively it can be estimated by dividing “Volume purged” / “Purge duration” | 2 l/min  15 / 8 = 1.9 l/min |
| Volume purged | Actual volume of water removed during purging in litres  Either measured, or calculated from “pumping rate” x “purge duration” | 15 |
| No of well volumes | Actual number of well volumes removed.  Calculated by dividing “Volume Purged / “Well Volume” | 15 / 12.3 = 1.2 |
| Depth to water after purge | Depth to water level recorded as metres below datum point (mbd) on completion of purging. | 5.3 |
| Pumped dry | Y - yes / N – No.  Yes if dry or if level has fallen below base of screened interval. | Y |

**Table A8.5e: Water quality measurements (if applicable)**

If stability of determinands is monitored during purging, then sufficient measurements need to be taken at different times in order to demonstrate that stability has occurred. At least 3 separate measurements should be provided to show readings at timed intervals.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Use flow through cell | Y - yes if used. N – No otherwise. | Y |
| min | Time in minutes since purging started.  At least 3 separate readings should be recorded on this form. Not all intermediate readings need be shown. | 2 |
| Vol | Vol of water removed at time of measurement (litres) | 0.5 |
| nVol | Number of well volumes removed | 1, 2, 3 etc |
| Temp (deg C) | Temperature in degrees centigrade. | 12.5 |
| pH | pH in pH units | 7.21 |
| EC (µS/cm ) | Electrical conductivity in µS/cm | 630 |
| DO (mg/l or %) | Dissolved oxygen expressed as mg/l or % saturation | 2.35 mg/l  28% |

**Table A8.5f: Quality Assurance**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Name | Name of person responsible for supervising or managing work. | Survey Person responsible for taking field measurements  QC Manager Person responsible for QC checks of data  Manager Person responsible for monitoring programmes |
| Date | Date when each task, including paperwork is completed. | 3/3/00 |
| Inits. | Initials of responsible person. | ABC |

**Table A8.5g: Data processing trail**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Schedule Completed | Date confirming when schedule has been checked against Monitoring Plan Specification and signed off as completed.  Include initials of person responsible for planning survey work. | 10/3/00, ABK |
| Data Validated | Date when data has been double-checked and validated.  Include initials of person responsible for validation. | 15/3/00, PDW |
| Computer Updated | Date when data has been entered into computer system (where used).  Include initials of person responsible for data entry. | 15/3/00, PDW |

**Table A8.5h: Example field sheet for recording borehole purging process**

**Table A8.5h(a): Borehole Purging Record Form**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Weather Conditions** |  |
| **Survey Reference** |  |
| **Survey Personnel** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.5h(b): Strategy and equipment used**

| **Strategy / Equipment** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Purge strategy  (Use code) |  |  |  |  |  |  |
| Purge equipment  (State type) |  |  |  |  |  |  |
| Dedicated pump?  (Y/N) |  |  |  |  |  |  |
| Flow measurement  (Method) |  |  |  |  |  |  |

**Table A8.5h(c): Monitoring point measurements and well volume estimate**

| **Measurements / well volume estimate** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Date of measurement |  |  |  |  |  |  |
| Liner ID  (mm) |  |  |  |  |  |  |
| Datum point |  |  |  |  |  |  |
| Depth to water  (mbd) |  |  |  |  |  |  |
| Depth to base  (mbd) |  |  |  |  |  |  |
| Depth of water  (metres) |  |  |  |  |  |  |
| Well volume  (litres) |  |  |  |  |  |  |
| 3 x well volume  (litres) |  |  |  |  |  |  |

**Table A8.5h(d): Purging record**

| **Purging** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Start time of purging  (hrs:mins) |  |  |  |  |  |  |
| End time of purging  (hrs:mins) |  |  |  |  |  |  |
| Purge duration  (mins) |  |  |  |  |  |  |
| Purging rate  (l/min) |  |  |  |  |  |  |
| Volume purged  (litres) |  |  |  |  |  |  |
| No of well volumes  (n) |  |  |  |  |  |  |
| Purged depth to water  (mbd) |  |  |  |  |  |  |
| Pumped dry?  (Y/N) |  |  |  |  |  |  |

**Table A8.5h(e): Water quality measurements (if applicable)**

|  | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Use flow through cell?  (Y/N) |  |  |  |  |  |  |

**Table A8.5h(f): Water quality measurements (if applicable) - Continued**

|  | **Min** | **Vol** | **nVol** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Temp (deg C) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
| pH |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
| EC(µS/cm) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
| DO(mg/l or %) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |

**Table A8.5h(g): Sample**

| **Sample** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** | **Monitoring Point**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Sample taken?  (Y/N) |  |  |  |  |  |  |

See separate sheet for sample collection data.

**Table A8.5h(h) – Quality Assurance and Data Processing Trail**

|  | **Name** | **Date** | **Inits** |
| --- | --- | --- | --- |
| **Quality Assurance: Survey** |  |  |  |
| **Quality Assurance: QC Manager** |  |  |  |
| **Quality Assurance: Manager** |  |  |  |
| **Data Processing Trail: Schedule Completed** |  |  |  |
| **Data Processing Trail: Data Validated** |  |  |  |
| **Data Processing Trail: Computer Updated** |  |  |  |

## A8.6 Sample collection form

An example form is provided as Table A8.6. This form could be used for recording information for sample collection of groundwater, leachate or surface waters.

**Table A8.6a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| SEPA Permit Number | Permit or Licence Reference Number. | WCC 123456 |
| Weather Conditions | Weather conditions on day of survey | Overcast and cloudy and cool following week of heavy rainfall. |
| Survey Reference | Survey Title | Quarterly Survey – June 2001  Six-Monthly Survey – September 2001. |
| Survey Personnel | Name(s) of survey personnel  Include company name if work undertaken by external contractor | AB Smith (AA Monitoring Co) |
| Monitoring Point or Sample Reference | Monitoring point reference number, or QC sample reference.  This is the sample ID which will be used on the laboratory analysis request form. QC sample  ID’s should not be apparent as such to the lab. | GW1, L1, GWA, etc |

**Table A8.6b: Strategy and equipment used**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Sample medium | Medium of sample collected | L Leachate  G Groundwater  S Surface water  Ld Duplicate leachate GWfb Groundwater field blank |
| Sample type | Type of sample taken. | C Composite (mixed  sample)  S Spot sample (taken at a specific depth without mixing)  U Uncertain |
| Sample equipment | Type of equipment used for sampling | Bailer  Inertial pump  Submersible  Bladder Pump |
| Dedicated pump | Y – Yes if installed at least 24 hours in advance of purging. N - No otherwise. | Y |
| Purge record | Y – Yes if written purge record on separate sheet or N - No otherwise. | Y |

**Table A8.6c: Sample collection information**

All monitoring points scheduled for monitoring should be included on this form. An explanatory comment should be provided where no data is obtained. This will facilitate with comparison against schedules set out in the Site Monitoring Plan.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Date of sample | Date sample collected | 1 / 1 / 03 |
| Time of sample | Time of sampling or period of sampling not always required. | 14:55  14:50 to 15:10 |
| Time since purge | Time since purging was completed | 2 mins  35mins |
| Depth to water | Depth to water level.  Recorded as metres below datum point (mbd) at time of sampling. | 5.3 |
| Pumping rate | Pumping rate used for sampling (litres per minute). | 0.5 l/min |
| Odour | Record any distinguishing smell | Sulphidal, hydrocarbons – tarry |
| Colour / appearance | Record any distinguishing water colouration (not sediment colour) or state if clear. | Red (iron-stained), clear |
| Sediment | Record presence of sediment | Fine silt particles  Sand and silt – 50% of unfiltered samples |
| Comments | Any general comments | - |

**Table A8.6d: Sample containers and field treatment**

Form allows for up to 5 sample containers with optional filtration or preservation methods.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Ref | Ref for type of sample container | 1, 2, 3 |
| Type | Type of container | PET PET (plastic) bottle  PE Polyethylene (plastic) bottle  GC Glass – clear  GB Glass – brown |
| Vol | Capacity of container in litres | 0.25, 1, 2.5 |
| Filt | Filter used for field filtration | None  ‘Purewater Co.’ 0.45 µm |
| Prsv | State preservative if preservative added to container. | H2SO4 |
| Lab Ref Number or Samples Taken | Record Lab No for each container (if used) or  Tick box under each monitoring point for each sample container filled. | L35709    √ |

**Table A8.6e: QC sample information**

Use this section to record the applicability of QC samples.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Tick if QC sample | Tick box if this is a QC sample. | √ |
| QC sample type | Specify QC sample type  For QC samples only | duplicate  ammonia standard GW field blank |
| Main samples referred to | State which main samples are covered by this QC sample.  For QC samples only | L1 all SW samples |
| QC samples referring to main sample | State which QC samples apply to this main sample.  For main samples only | L1d GWfb |

**Table A8.6f: Water quality measurements**

If determinands were monitored (for stability) during purging, then records will be the same as those taken at the end of purging. Otherwise separate measurements are needed on this form.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Use flow through cell | Y - yes if used. N – No otherwise. | Y |
| Temp (deg C) | Temperature in degrees centigrade. | 12.5 |
| pH | pH in pH units | 7.21 |
| EC (µS/cm ) | Electrical conductivity in µS/cm | 630 |
| DO (mg/l or %) | Dissolved oxygen expressed as mg/l or % saturation | 2.35 mg/l  28% |
| Eh (mV) | Redox potential recorded as millivolts. | -55 |

**Table A8.6g: Quality Assurance**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Name | Name of person responsible for supervising or managing work. | Survey Person responsible for taking field measurements  QC Manager Person responsible for QC checks of data  Manager Person responsible for monitoring programmes |
| Date | Date when each task, including paperwork is completed. | 3/3/00 |
| Inits. | Initials of responsible person. | ABC |

**Table A8.6h: Data processing trail**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Schedule Completed | Date confirming when schedule has been checked against Monitoring Plan Specification and signed off as completed.  Include initials of person responsible for planning survey work. | 10/3/00, ABK |
| Data Validated | Date when data has been double-checked and validated.  Include initials of person responsible for validation. | 15/3/00, PDW |
| Computer Updated | Date when data has been entered into computer system (where used).  Include initials of person responsible for data entry. | 15/3/00, PDW |

**Table A8.6i: Example field sheet for recording collection of water samples**

**Table A8.6i(a): Sample Collection Form**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **SEPA Permit Number** |  |
| **Weather Conditions** |  |
| **Survey Reference** |  |
| **Survey Personnel** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.6i(b): Strategy and equipment used**

| **Strategy / Equipment** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Sample type  (G/L/S/O) |  |  |  |  |  |  |
| Sample objective  (Use code) |  |  |  |  |  |  |
| Sample equipment  (State type) |  |  |  |  |  |  |
| Dedicated pump?  (Y/N) |  |  |  |  |  |  |
| Purge record?  (Y/N) |  |  |  |  |  |  |

**Table A8.6i(c): Sample collection information**

| **Sample** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** | **Monitoring Point or Sample Reference No**  **Enter Ref here.** |
| --- | --- | --- | --- | --- | --- | --- |
| Date of sample |  |  |  |  |  |  |
| Time of sample  (hrs:mins) |  |  |  |  |  |  |
| Time since purge  (mins) |  |  |  |  |  |  |
| Depth to water  (mbd) |  |  |  |  |  |  |
| Pumping rate  (l/min) |  |  |  |  |  |  |
| Odour |  |  |  |  |  |  |
| Colour / appearance |  |  |  |  |  |  |
| Sediment |  |  |  |  |  |  |

**Table A8.6i(d): Sample collection information - Comments**

| **Comments** |
| --- |
|  |

**Table A8.6i(e): Sample containers and field treatment**

| **Ref** | **Type** | **Vol** | **Filt** | **Prsv** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |

**Table A8.6i(f): QC Sample information**

|  | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** |
| --- | --- | --- | --- | --- | --- | --- |
| Tick if QC sample |  |  |  |  |  |  |
| QC sample type |  |  |  |  |  |  |
| Main samples referred to |  |  |  |  |  |  |
| QC samples referring to main sample |  |  |  |  |  |  |

**Table A8.6i(g): Water quality measurements (if applicable)**

|  | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** | **Lab Ref No or Samples Taken**  **(Tick box)** |
| --- | --- | --- | --- | --- | --- | --- |
| Use flow through cell?  (Y/N) |  |  |  |  |  |  |
| Temp  (deg C) |  |  |  |  |  |  |
| pH |  |  |  |  |  |  |
| EC  (µS/cm) |  |  |  |  |  |  |
| DO  (mg/l or %) |  |  |  |  |  |  |
| Eh  (mV) |  |  |  |  |  |  |

**Table A8.6i(h) – Quality Assurance and Data Processing Trail**

|  | **Name** | **Date** | **Inits** |
| --- | --- | --- | --- |
| **Quality Assurance: Survey** |  |  |  |
| **Quality Assurance: QC Manager** |  |  |  |
| **Quality Assurance: Manager** |  |  |  |
| **Data Processing Trail: Schedule Completed** |  |  |  |
| **Data Processing Trail: Data Validated** |  |  |  |
| **Data Processing Trail: Computer Updated** |  |  |  |

## A8.7 Laboratory analysis request form

A form is required to indicate sample identities and analysis requirements to the laboratory. This should be supplied by the laboratory and should include space for information (e.g. added preservative), comments (e.g. likely concentration) and special requests (e.g. a requirement for immediate subsampling and preservation) relating to each sample.

## A8.8 Chain of custody document

An example form is provided as Table A8.7. These forms record the movement of samples from the point of sample to the laboratory and are essential where legal issues are involved.

**Table A8.7a: Heading information**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Page \_ of \_ | Sequential sheet number for each register. | 1 of 3 |
| Site Name | Name of landfill site.  It is preferable to use the name stated on the permit unless some other name is commonly used. | Mountain Top Landfill Site |
| Site Operator | The named permit holder and / or landfill operator. | ABC Landfill Co. |
| Survey Reference | Survey Title | Quarterly Survey – June 2001  Six-Monthly Survey – September 2001 |
| Organisation Ref | Organisation Reference Code.  Use a project code or other identifiable code relevant to the organisation responsible for the samples. Leave blank otherwise. | L1530 / 47 |
| Laboratory Ref | Laboratory Reference code.  Use a project code or other identifiable code relevant to the laboratory receiving the samples.  Leave blank otherwise. | HA/4508 |
| Sampling Date(s) | Date or period of sampling  Date or dates over which sampling was carried out. | 5/4/2000  5/4 to 7/4 2000 |

**Table A8.7b: Person and Organisation responsible for samples**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Person Responsible | Name | JG Smith |
| Position | Position of Person Responsible for samples | Environmental Scientist |
| Signature | Signature of Person Responsible for samples | - |
| Organisation | Name of Organisation responsible for samples | A1 Sampling Co Ltd |
| Address | Address of Organisation responsible for samples | 3 Market Street, Moniton, Landfillshire MT43 6AS |
| Tel No | Telephone number | 0107 1234567 |
| Fax No | Fax number | 0107 1234568 |
| email | email address | Sample.team@A1Sample.co.uk |

**Table A8.7c: Sample identification**

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| Sample Container Ref | Ref Number for each individual sample container  Use lab ref number if provided with sample containers. Numbers should be a unique and correspond with those used on Sample Form (see Table A8.6) | L12507 |
| Monitoring Point Reference | Monitoring point reference number.  Links each sample container to a monitoring point. | GW1, L1, GWA |
| Date sampled | Date sample collected | 1 / 1 / 03 |
| Time sampled | Time of sampling or period of sampling | 14:55  14:50 to 15:10 |
| Sample type | Type of sample collected | L Leachate  G Groundwater  S Surface water |
| Container Type | Type of container | PET PET (plastic) bottle  PE Polyethylene (plastic) bottle  GC Glass – clear  GB Glass – brown |
| Container Size | Capacity of container in litres | 0.25, 1, 2.5 |
| No and type of packages | Describe packages | 3 x cool boxes 1 x milkcrate |
| Describe seals or markings | Describe sealing used for security | Wrapped with brown packaging tape |

**Table A8.7d: Chain of custody and copy forms**

This part of the form should record the passage of samples from the person / organisation taking the samples to their receipt at the laboratory. The number of companies / individuals involved will vary, and could simply involve direct transfer from the sampler to the laboratory without separate packaging or the use of a courier. Details on the form should be modified accordingly. For legal samples, it is vital that a continuous traceable chain is formally recorded.

| **Field** | **Description (with explanatory text)** | **Examples** |
| --- | --- | --- |
| From  (Organisation) | Organisation responsible for relinquishing samples | A1 Sampling Co Ltd |
| Relinquished by | Name and signature of person handing over samples. | AB Smith |
| Form Copy No | Copy Ref of Signed form  Code used to identify copy of form signed. This copy should be retained by the person / organisation relinquishing the sample. | 2, 3 |
| Date | Date samples were transferred | 3/3/00 |
| Time | Time samples were transferred | 16:35 |
| To  (Organisation) | Organisation responsible for receipt of samples.  Name of company – e.g. a courier. For legal samples transfers internally within companies should also be recorded on this form. | EverFast Couriers plc |
| Received by | Name and signature of person receiving samples. | XY Jones |

**Table A8.7e: Example chain of custody form**

**Table A8.7e(a): Chain of Custody Record**

|  |  |
| --- | --- |
| **Site Name** |  |
| **Site Operator** |  |
| **Organisation Ref (e.g. Project Number)** |  |
| **Laboratory Reference** |  |
| **Survey Reference** |  |
| **Sampling Date(s)** |  |
| **Page Number** | \_\_\_\_\_\_ of \_\_\_\_\_\_ |

**Table A8.7e(b): Person and Organisation Responsible for Samples**

|  |  |
| --- | --- |
| **Person Responsible** |  |
| **Position** |  |
| **Signature** |  |
| **Organisation** |  |
| **Address** |  |
| **Tel No** |  |
| **Fax No** |  |
| **Email** |  |

**Table A8.7e(c): Sample Identification**

| **Sample Container Ref** | **Mon Point Ref** | **Date Sampled** | **Time Sampled** | **Sample Type** | **Container Type** | **Container Size**  **(litres)** | **Comments** |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |

**Table A8.7e(d): Packages**

| **No and type of packages prepared for transfer** | **Describe any seals or markings applied to packaging or samples** |
| --- | --- |
|  |  |

**Table A8.7e(e): Chain of Custody and Copy Forms**

| **From**  **(Organisation)** | **Relinquished by**  **(Print name with / signature)** | **Form Copy Number** | **Date** | **Time** | **To**  **(Organisation)** | **Received by**  **(Print name with / signature)** |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 2 |  |  |  |  |
|  |  | 3 |  |  |  |  |
|  |  | 4 |  |  |  |  |
|  |  | 5 |  |  |  |  |

1.The laboratory should return the Top Sheet of the form complete with all signatures to the organisation responsible for the samples as soon as samples are received at the laboratory.

2.Copy 1 of this form should be enclosed with samples in a sealed envelope prior to despatch to the laboratory.

3.The organisation relinquishing the samples should retain the form copy number indicated above.

# Appendix 9: Example Monitoring Protocols

## A9.1 Introduction

Two protocols are produced in this Appendix as examples:

* A protocol for obtaining a sample from a borehole and
* A protocol for decontamination of equipment.

The sampling protocol is partly adapted from Blakey et al. 1997 but has been revised and restructured.

Other protocols and information relating to issues such as surface water and biological samples can be derived from monitoring methods described by the Standing Committee of Analysts, 1996.

## A9.2 Structure of monitoring protocols

### A9.2.1 Generic protocol structure

A monitoring protocol should take account of all the practical tasks necessary in order to plan, implement and complete a procedure in a consistent and reproducible manner. The structure presented below identifies the key tasks in a protocol and provides a brief outline of issues to be considered under each task heading:

* Planning:
  + Client instructions.
  + Monitoring objectives.
  + Site and sample location plan.
  + Sample location details.
  + Access arrangements and routes.
  + Special procedures required for handling contaminated water.
  + Sample specification and laboratory co-ordination.
  + Personnel and time needed.
  + General health and safety arrangements.
  + Notifications.
* Equipment:
  + Miscellaneous items.
  + Personal protective equipment.
  + Field measurement equipment.
  + Sampling equipment.
  + Sample containers, transfer vessels and crates.
  + Cleaning equipment.
  + Contaminated water storage and disposal equipment.
* Field Documentation:
  + Job information documents.
  + Monitoring procedure documents.
  + Transport, sample submission and chain of custody documents.
* Pre-use checks:
  + Decontamination of equipment.
  + Functionality of equipment.
  + Cleaning and decontamination of equipment.
  + Pre-site paperwork.
* Monitoring procedure (e.g. taking a water sample from a borehole):
  + Physical measurements.
  + Equipment assembly and installation.
  + Site calibration of equipment.
  + Borehole purging.
  + Field instrument measurements.
  + General sample collection procedure.
  + Specialist samples.
  + Quality control samples.
* Completion and decontamination:
* Equipment recovery.
* Cleaning and decontamination.
* Secure monitoring location.
* Disposal of contaminated purge water.
* Sample labels, packaging, chain of custody and delivery:
  + Labelling and packaging of samples.
  + Chain of custody.
  + Delivery arrangements.
* Additional notes. additional instructions for special circumstances

## A9.3 Example protocol for sampling groundwater or leachate from a monitoring borehole by pumping

### A9.3.1 Planning

**Table 9.1a: Management / Client instruction**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Client / site details with contact telephone number |  |
| 2 | Project reference number / details |  |
| 3 | Available budgets |  |

**Table 9.1b: Monitoring objectives**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Agree monitoring objectives with management/ client (in writing) |  |
| 2 | Define the need for specialist procedures for sampling and analysis in the light of objectives |  |
| 3 | Redraft monitoring protocol to meet monitoring objectives (if necessary) |  |

**Table 9.1c: Site and sample location plan**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Site map showing borehole locations with reference numbers |  |

**Table 9.1d: Sample location details**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Obtain and summarise all information relating to the monitoring points necessary for sampling e.g. (for boreholes):  Borehole depth, diameter, screened interval, approx. water level, headworks details, details of any dedicated pumping system. |  |
| 2 | Collate and summarise any other relevant information from previous surveys where relevant  e.g. Purging and sampling rates / drawdown response to pumping / time taken to purge and sample |  |

**Table 9.1e: Access arrangements and routes**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Check with client the access routes and ground conditions for field vehicles / personnel |  |
| 2 | Confirm any site-specific Health and Safety instructions (in writing) |  |
| 3 | Agree any other conditions of entry to the site or off-site monitoring points. |  |

**Table 9.1f: Special procedures required for handling contaminated water**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Determine method of disposal for purge water.  Where doubt exists in relation to disposal of potentially contaminated waters, advice should be sought from SEPA. |  |
| 2 | Obtain consents for disposal of purge water (if required) |  |
| 3 | Prepare health and safety procedures for monitoring personnel for handling contaminated purge waters |  |
| 4 | Prepare instructions for monitoring personnel for disposal of contaminated purge water |  |

**Table 9.1g: Sample specification and laboratory co-ordination**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Discuss the sample analytical requirements with the analyst e.g.  Determinands, sample type and condition, sample containers, sample storage, reception arrangements.  Other sample requirements like filtration, preservation, bottle headspace should also be confirmed. |  |
| 2 | Define quality control procedures and samples to be taken. |  |
| 3 | Define arrangements for handling and analysis of contaminated samples |  |
| 4 | Obtain quotation (where necessary) |  |
| 5 | Confirm all arrangements in writing including delivery and/or collection of prepared sample containers. |  |

**Table 9.1h: Personnel and time needed**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Define number of monitoring personnel and experience / competence needed |  |
| 2 | Define number of days required to obtain all samples |  |
| 3 | Confirm budgets |  |

**Table 9.1i: General Health and Safety arrangements**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Prepare a Site Operating Procedure (SOP) based on your organisations Health and Safety policy statement  The SOP should take account of the employer’s responsibility with respect to the Control of Substances Hazardous to Health (COSHH) Regulations 1988. Each SOP should be assigned a specific hazard/risk code, which can be used to identify appropriate Personal Protective Equipment (PPE) for the task. |  |

**Table 9.1j: Notifications**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Notify all interested parties of arrangements for sampling. e.g.  Client, site manager, SEPA, landowners etc. |  |

### A9.3.2 Equipment

**Table 9.2a: Miscellaneous items**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Vehicle (specify if 4WD or specialist transport needed): |  |
| 2 | Keys for monitoring points and site and other points of access. |  |
| 3 | Tool kit |  |
| 4 | For monitoring equipment and to help with access to borehole headworks. |  |

**Table 9.2b: Personal protective equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Basic PPE equipment  e.g. Overalls, safety boots, hard hat, high visibility jacket, ear defenders, goggles, disposable gloves, protective gloves. |  |
| 2 | Other PPE equipment (specified by Health and Safety assessment)  e.g. face masks and filters etc. |  |
| 3 | Wet weather or cold weather clothing  e.g. overtrousers, kagoule, thermals, thermal gloves, etc. |  |
| 4 | Communications equipment  e.g. mobile phone / site radio (check site-specific safety aspects for use)  If working alone make arrangements for confirmed communication with third party |  |

**Table 9.2c: Field measurement equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Groundwater level dipper  Check length is sufficient for all monitoring points. |  |
| 2 | Weighted plumb line  Check length is sufficient for all monitoring points. |  |
| 3 | Tape measure |  |
| 4 | Temperature meter and probe |  |
| 5 | pH meter, including probe and calibration solutions |  |
| 6 | Conductivity meter including probe and calibration solutions |  |
| 7 | Dissolved oxygen (DO) meter including probe and calibration solutions |  |
| 8 | Eh meter including probe and calibration solutions |  |
| 9 | Flow through cell  Including tubing and coupling attachments |  |
| 10 | Beaker(s) for field measurements (where flow through cell not available) |  |
| 11 | Deionised or distilled water in rinse bottle |  |

**Table 9.2d: Sampling equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Pumping and sampling equipment.  e.g. Bailers, reel and lifting cable  Inertial pumping equipment including valves, tubing, extension tubing, actuator, tools  Submersible pumping equipment including generator, control box, hose and reel  Bladder pumping equipment including air supply, control box, hose and reel  Suction pump equipment including, suction hose, discharge hose and tools  Peristaltic pumping equipment including silicon sample tubing |  |
| 2 | Flow or volume measuring equipment  e.g. Graduated bucket or drum  Bucket and stopwatch (for flows up to approx. 30 l/ min)  Cumulative flow meter (for steady pumped discharges) |  |

**Table 9.2e: Sample containers, transfer vessels and crates**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Crates for carrying equipment to and from monitoring points |  |
| 2 | Sample bottles (supplied by lab). |  |
| 3 | Quality control samples and containers  e.g. field standards and blanks.  (NB At least 1 duplicate sample should be obtained for every 10 samples taken) |  |
| 4 | Filtration and preservation equipment  e.g. disposable cartridge filters, preservative solutions (where supplied by lab outside of supplied bottles) |  |
| 5 | Transfer sample vessels  e.g. beakers, funnels |  |
| 6 | Packaging crates  e.g. Cool boxes containing pre-frozen freezer packs |  |

**Table 9.2f: Cleaning equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Sample area cleaning equipment  e.g. plastic sheet, paper towels |  |
| 2 | 5 litre container of clean water  For rinsing equipment, probes etc. |  |
| 3 | Equipment decontamination solutions and vessels |  |

**Table 9.2g: Contaminated water storage and disposal equipment**

(NB if purge water has to be disposed elsewhere for treatment, separate arrangements should be made in advance of site work for storage of water prior to disposal)

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Temporary pumping storage reservoir  e.g. 200 litre plastic bins |  |
| 2 | Purge water discharge equipment  e.g. siphon tubing with inertial foot valve / suction pump and hose |  |

### A9.3.3 Field Documentation

**Table 9.3a: Job information documents**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Site plan showing monitoring locations |  |
| 2 | Monitoring point register |  |
| 3 | Copy of monitoring protocols |  |

**Table 9.3b: Monitoring procedure documents**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Field notebook |  |
| 2 | Equipment calibration form(s)  e.g. for field instruments pH, EC, DO, Eh |  |
| 3 | Purging record form |  |
| 4 | Sampling record form |  |

**Table 9.3c: Transport, sample submission and chain of custody documents**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Laboratory submission forms  e.g. Laboratory labels (if separate from bottles)  Laboratory manifest/ analysis request forms |  |
| 2 | Chain of custody forms (if needed) |  |
| 3 | Courier manifest (if needed) |  |

### A9.3.4 Pre-use checks / decontamination of equipment

**Table 9.4a: Functionality of equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Check all equipment is operational.  e.g. check batteries, probes, meters etc are in working order |  |
| 2 | Check calibrate equipment  e.g. dip meters, pH, temperature, conductivity, Eh and DO probes.  Ensure that calibration and standard solutions are in date for use during the sampling exercise. |  |

**Table 9.4b: Clean and decontaminate equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Clean all equipment  e.g. all equipment used to contact samples should be cleaned |  |
| 2 | Decontaminate equipment  e.g. any equipment used for previous sampling should be decontaminated (see separate procedure) |  |
| 3 | Familiarise monitoring personnel with site cleaning and decontamination procedures  Where special procedures are required, monitoring personnel should be informed fully at this stage. |  |

**Table 9.4c: Pre-site checks**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Complete sample identification information onto sample bottle labels  Check details on pre-printed labels supplied by laboratory (particularly where these are linked to computerised reception arrangements at laboratory). Labels should be placed on the container itself rather than the lid. |  |
| 2 | Define calibration frequency for each instrument  e.g. EC – am / midday / pm pH – at each monitoring point DO – at each monitoring point etc |  |
| 3 | Check all equipment into vehicle |  |

### A9.3.5 Monitoring procedure (e.g. taking a water sample from a borehole)

**Table 9.5a: Physical measurements**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Unlock / remove protective cover.  Where dedicated sampling equipment is installed in a borehole, this should not be disturbed until after completion of physical measurements in order to avoid displacement of the standing water level. |  |
| 2 | Observe and record damage to condition of surface seals, headworks and lining. |  |
| 3 | Measure and record organic vapour reading (if required)  Use a photo-ionisation detector or organic vapour detector. |  |
| 4 | Measure and record specific gas concentrations (if required)  e.g. methane, carbon dioxide, hydrogen sulphide Use a flammable gas or specific gas detector |  |
| 5 | Measure and record depth and thickness of any floating product layer (if required) Using an oil water interface probe. |  |
| 6 | Describe and record height of datum point used for measurements above ground level Use tape measure or dipper. |  |
| 7 | Measure and record borehole dimensions and water level relative to datum  e.g. lining diameter (d), depth to water (dip), depth to base of borehole (depth)  Using a groundwater level dipper for water levels / Use plumb line, for depth measurements  If borehole dimensions vary significantly from borehole records, particularly if the screened section of the borehole is blocked, take advice before sampling. Highlight this information on standard field forms. |  |
| 8 | Calculate and record borehole water volume:  Length of water column in borehole (L) = depth – dip  1 x borehole volume = π d2.L / 4 (using consistent units). |  |
| 9 | Calculate and record purge volume (if required)  e.g. 3 x borehole volume |  |

**Table 9.5b: Equipment assembly and installation**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Lay out and assemble all purging, field measurement and sampling equipment  Use clean plastic sheet wherever practical or necessary  Separate sampling, field measurement and purging equipment. |  |
| 2 | Lay out all sample bottles and decontaminated sampling equipment in an area free from possible sources of contamination and separate from other equipment |  |
| 3 | Ensure sample bottle labels are correct and firmly attached. |  |
| 4 | Layout and separate all specialist sampling equipment and containers  Where volatiles are being sampled cleanliness and separation of all sampling equipment from volatile sources such as petrol fumes is vital. Quality control samples should be distributed as necessary for this purpose. |  |
| 5 | Layout discharge point for purge water  e.g. area of ground or ditch set aside for clean discharges unrestored landfill area set aside for leachate discharges storage containers to receive contaminated purge water  NOTE: Any discharges to surface should be directed at a sufficient distance from the borehole to prevent water returning to the borehole head works. |  |
| 6 | Install or adjust purging / sampling equipment to appropriate depth in borehole  e.g. for dedicated equipment already set at a fixed intake level: - do not disturb. for other dedicated equipment: - lift or lower gently to pumping depth. for non-dedicated equipment: - lower to pumping depth.  Depending on equipment used, secure or mark pumping position (e.g. by locking the cable drum or by using a catch-plate).  Record intake position of pump in borehole |  |
| 7 | Connect pumping equipment to power and control sources  e.g. generator or actuator or compressor and any control units |  |

**Table 9.5c: Site calibration of equipment**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Re-calibrate all equipment on site as required  e.g. EC, pH, DO, Eh – at each monitoring point or 2 to 3 times per day. Record on calibration record form. |  |

**Table 9.5d: Borehole purging**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Connect discharge hose from borehole pump outlet to discharge point or storage containers |  |
| 2 | Set up discharge flow measurement arrangements  e.g. connect discharge to flow meter  prepare personnel with bucket / stopwatch |  |
| 3 | Connect discharge to flow-through cell (if used to monitor stability of water quality during purging) Flow through cell should be set-up with field instruments already connected. |  |
| 4 | Start pumping and adjust pumping rate  e.g. match to predetermined purge rates match to borehole yield run pump at max capacity |  |
| 5 | Measure and record as necessary  e.g. discharge volume and flow rate  field measurements (Temp, pH, EC, DO etc) water level |  |
| 6 | Continue pumping and recording measurements until purging criteria met  Reduce pumping rate or cease pumping at end of purge |  |
| 7 | Measure and record water level on completion of purge  (Where siltation is likely to occur, also record depth to base of borehole) |  |

**Table 9.5e: Field instrument measurements**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Measure and record field measurements immediately before or at the time of sampling  e.g. temperature, pH, EC, DO  DO and Eh measurements should only be carried out in a flow though cell pH, temperature and EC may be recorded in a beaker |  |

**Table 9.5f: General sample collection procedure**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Measure and record water level before sampling.  Ensure water level is not below any criteria specified by sampling objectives. Note in particular where the level of water is lower than the screen intake level in the borehole. |  |
| 2 | Reduce pumping rate to 1 litre/min or less. |  |
| 3 | Take samples not requiring field filtration or preservation  Fill the sample bottles direct from the discharge tubing wherever possible. Rinse the bottles with sample water and fill to the top leaving no air space. Check sample label, adding any necessary additional information. |  |
| 4 | Take samples requiring preservation without field filtration  Fill as above but do not rinse bottles and only fill to level in bottle as instructed by laboratory. |  |
| 5 | Take samples requiring field filtration without preservation  Use filtration device according to instructions and fill directly from filter / filtration device into sample bottle. Rinse the bottle with filtered sample water and fill to the top leaving no air space. Check sample label, adding any necessary additional information.  Filtration for metal determinands is normally through a 0.45 µm membrane filters (after discarding the first aliquot of filtered sample). |  |
| 6 | Take samples requiring field filtration and preservation  Filter and fill as above but do not rinse bottles and only fill to level in bottle as instructed by laboratory. |  |

**Table 9.5g: Specialist samples - volatiles**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Reduce pumping rate to 0.5 litre/min or less. |  |
| 2 | Take sample ensuring no aeration at discharge point from pump  e.g. base-fitting valve discharge from bailer (not poured) siphon discharge from inertial pump low flow discharge from submersible pump direct discharge from bladder pump |  |
| 3 | Fill glass vial or other sample container to the brim and screw on the cap with PTFE-lined septum. Check sample, adding any necessary additional information.  There should be no headspace within the vial. |  |
| 4 | Immediately store the vials upside-down in a cool-box to minimise the loss of volatiles. |  |

**Table 9.5h: Quality control samples**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Collect sample duplicate (as required)  Collect full set of duplicate samples following sample procedures set out above.  1 in 10 samples is the recommended ratio for duplicate samples. |  |
| 2 | Collect field standard and field blank samples (as required)  These samples are rinsed through the sampling equipment into containers identical to the main samples, immediately after sampling. Check sample labels, adding any necessary additional information. |  |
| 3 | Any trip standards and blanks should remain unopened unless specified otherwise. Check sample labels, adding any necessary additional information.  Trip standards and blanks are samples prepared in the laboratory, transported to the field and returned to the laboratory. They are generally never opened although some require field preservation. They provide a control for the field standards and blanks. |  |

### A9.3.6 Completion and decontamination

**Table 9.6a: Equipment recovery, cleaning and decontamination**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Withdraw non-dedicated equipment from borehole taking care not to damage equipment or borehole. |  |
| 2 | Disassemble the equipment on the plastic sheet, rinse with clean, deionised or distilled water as appropriate and pack the equipment away. |  |
| 3 | Rinse all non-disposable sampling accessories (e.g. bailers) with organic-free and/or deionised water before packing them away. |  |
| 4 | Remove all storage and transfer equipment from site. |  |

**Table 9.6b: Secure monitoring location**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 |  |  |

**Table 9.6c: Disposal of contaminated purge water**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Dispose contaminated purge water  e.g. Disposal off-site: Ensure all containers are made safe for transport and disposal / make arrangements with disposal company to collect  Disposal to alternative site location: transport or pump to on-site disposal area (e.g. open landfill area, leachate sump)  Returned to adjacent irrigation point / leachate borehole: Siphon or pump water to disposal point |  |
| 2 | Dispose of heavily contaminated or disposable equipment. |  |

### A9.3.7 Sample labels, packaging, chain of custody and delivery

**Table 9.7a: Labelling and packaging of samples**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Clean the outer surface of all sample containers with paper towels (dye free) using deionised or organic free water, as necessary. |  |
| 2 | Check that all sample bottles are labelled correctly and securely. |  |
| 3 | Seal each sample container as appropriate. e.g.  by wrapping tape around lid. (e.g. Teflon tape on volatile samples. / use PVC tape on all other samples). |  |
| 4 | Protect containers from breakage as appropriate  e.g. place polynet over glass containers / wrap in bubble pack and securely tape bubble pack with tape. |  |
| 5 | Place all samples in storage and transport containers  e.g. cool boxes containing freezer packs (where preservation requires) crates or cartons |  |

**Table 9.7b: Documentation and Chain of custody**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Record all samples taken on sample collection forms. |  |
| 2 | Complete laboratory analysis request forms and place one copy inside sample transport containers. |  |
| 3 | Prepare chain of custody documentation (if required) and seal one copy inside sample transport containers. |  |
| 4 | Seal all transport containers with tape. |  |
| 5 | Sign and date custody seals (if required) and secure over openings of all transport containers. |  |

**Table 9.7c: Delivery**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Prepare courier manifest. |  |
| 2 | Hand over sample to courier or transport directly to laboratory  All samples should be delivered to a laboratory within a stated time period from sampling (ideally on the same day of sampling).  Delivery time will be dependent on the range of analysis requested in accordance with sample holding times determined by preservation, storage and transport arrangements.  Chain of custody documents should be completed each time samples are transferred to another person or company. |  |
| 3 | Deliver to laboratory  Delivery of samples should be receipted by laboratory. Chain of custody document should be completed where necessary. |  |

### A9.3.8 Additional notes

**Table 9.8a: Additional instructions for special circumstances**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Equipment used for sampling “contaminated” water should be appropriately marked and must be stored and maintained separately from equipment used for “clean” water samples. |  |
| 2 | Where dedicated sampling equipment for each borehole is not available, and previous monitoring data demonstrate that a range of levels of contamination will be encountered during a sampling exercise, attempt to commence the sampling exercise with the least contaminated borehole, finishing with the most heavily contaminated borehole. |  |
| 3 | For large diameter observation boreholes, a dual pump array for purging and sampling may be required. |  |
| 4 | Conditions in the borehole (e.g. presence of silt or other heavy particulates) may affect the temporal variations in the data or be responsible for systematic trends. Where changes in borehole conditions are encountered, monitoring personnel must discuss observations with their supervisor prior to sampling. |  |

## A9.4 Example protocol for decontamination of equipment

The following protocol is based on American Society for Testing Material (ASTM) standard D5088.

### A9.4.1 Planning

**Table 9.9: Decontamination objectives**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 |  |  |

### A9.4.2 Equipment

**Table 9.10: Reagents**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Detergent – non-phosphate detergent solution  e.g. Alquinox, Liquinox, Decon 90 |  |
| 2 | Acid rinse (inorganic desorbing agent)  e.g. 10% nitric or hydrochloric acid solution made from reagent grade nitric or hydrochloric acid and deionised water |  |
| 3 | Solvent rinse (organic desorbing agent)  e.g. isopropanol, acetone or methanol (pesticide grade). |  |
| 4 | Control rinse water  e.g. should be from a water supply of known chemical composition |  |
| 5 | Deionised water  e.g. organic-free reagent grade |  |

### A9.4.3 Cleaning of equipment in contact with water sample

**Table 9.11a: Minimum procedure**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Minimum Procedure  Wash equipment in detergent solution. |  |
| 2 | Rinse with control rinse water |  |

**Table 9.11b: Inorganic analyses – rigorous procedure**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Wash equipment in detergent solution using a brush made of inert material to remove any particles or surface film.  Where a brush is inadequate or cannot be used, detergent solution should be circulated through the equipment (e.g. through sample tubing or pumps) |  |
| 2 | Rinse or flush equipment thoroughly with control water |  |
| 3 | Rinse or flush with inorganic desorbing agent |  |
| 4 | Rinse or flush with control water |  |

**Table 9.11c: Organic analyses – rigorous procedure**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Wash equipment in detergent solution using a brush made of inert material to remove any particles or surface film.  Where a brush is inadequate or cannot be used, detergent solution should be circulated through the equipment (e.g. through sample tubing or pumps) |  |
| 2 | Rinse or flush equipment thoroughly with control water |  |
| 3 | Rinse or flush with inorganic desorbing agent (not necessary if samples will not be used for inorganic chemical analyses) |  |
| 4 | Rinse or flush with control water |  |
| 5 | Rinse or flush with organic desorbing agent |  |
| 6 | Rise or flush with deionised water |  |
| 7 | Allow equipment to air-dry before next use |  |
| 8 | Wrap equipment for transport with inert material until used for sampling  e.g. aluminium foil or plastic wrap |  |

### A9.4.4 Cleaning of other non-sample contact equipment

**Table 9.12: General procedure**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Clean equipment with portable power washer or steam cleaning machine or  (for smaller items)  Hand wash with brush using detergent solution. |  |
| 2 | Rinse with control rinse water. |  |

### A9.4.5 Record keeping

**Table 9.13: General procedure**

| **No.** | **Instruction** | **Check** |
| --- | --- | --- |
| 1 | Record date / time and decontamination procedure used for each item of sample equipment. |  |
| 2 | Record individuals involved in procedure. |  |
| 3 | Record details of type and name of reagents used, including rinse water. |  |

## References

American Society for Testing and Materials (1997). *ASTM Standards on environmental sampling*. ASTM. USA. Ref: 03-418097-38. ISBN: 0-8031-1835-X.

Environment Agency (1998). *Quality management system for environmental sampling: Groundwater sampling*. National Sampling Procedures Manual. Environment Agency. Bristol. Report No. ES 006. In preparation.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

# Appendix 10: Sampling Equipment

## A10.1 Introduction

The content of the following Appendix is drawn from a number of sources, but acknowledgement is particularly given to Blakey, N.C. et al., 1997 from which some of the following sections are reproduced or paraphrased.

## A10.2 Level measurement equipment

### A10.2.1 Water level and depth measurement devices for use in boreholes

**Measurement equipment**

**Electric tapes**

Used for recording water and leachate level in vertical structures. An electrical circuit is formed when the contacts on the probe are submerged in water.

In highly conductive waters (e.g. leachates) the contact may remain formed for a long time and can even be set off by moisture in the structure giving inaccurate results. This can sometimes be overcome by the use of a sensitivity switch and by shrouding the probe.

In low conductivity waters (e.g. some groundwaters) the conductivity of the water may be insufficient to form the contact. This can also be overcome by the use of a sensitivity switch.

Tapes can stretch - particularly in hot environments. They should be periodically calibrated against a tape not used for dipping purposes. Where lengths are inaccurate by more than 1 cm in 30m (0.03%) the tape should be replaced.

Tapes can break due to catching on snags. When repairs are made in which a short length (e.g. 1m) is cut-off it is easy to misread measurements. To avoid confusion, it is recommended that any cuts are made at lengths of at least 5 metres and preferably at 10 metres.

**Plumb lines**

Depth to the base of a monitoring point is best measured by the use of a weighted plumb line. In practice this measurement is commonly made using electric water level tapes (and some manufacturers have developed probes which electronically signal when the base is reached). Most water level tapes are not pressure-rated to be submerged below water level without the possibility of leakage breaching the probe seals. They are rarely sufficiently weighted to be able to reliably confirm the base level of deeper monitoring points, which can compromise the accuracy of measurement.

Any electric tape or plumb line used for depth measurement should be:

* capable of recording levels to an accuracy of 1 cm in 30m (0.03%) and
* calibrated at least annually against a tape of constant length plastic-coated electric tapes can stretch, particularly where affected by higher temperature leachates or exposed to high ambient temperatures for prolonged periods.

Any tape which is unable to meet the specified measurement accuracy (i.e. to within 0.03%) should be replaced.

**Floats**

Not commonly used except in water level recorders.

**Transducers**

Pressure transducers record pressure in a fluid at a point of measurement. Combined with data-loggers they are ideal for remote locations or where continuous records need to be obtained. Data can be downloaded from data loggers direct to computer.

Accuracy and reliability of transducers is variable, and it is important to install a transducer of appropriate specification for the range of depths to be measured. They should be frequently calibrated against measurements using dip meters and should be capable of measuring to an accuracy similar to that of a dip tape (i.e. 0.03%).

## A10.3 Borehole sampling equipment

### A10.3.1 Introduction

Flow rates for purging boreholes should be high enough to be time efficient without causing significant drawdown of the water level or disturbance of the sample. Flow rates used during sampling should be low to prevent agitation / aeration of the sample during transfer. Barcelona et al. (1984) recommend flow rates not greater than 100 ml/min for sampling volatile chemical constituents. As with all sampling equipment, selection must be site-specific, and consideration must be given to determinands sampled.

There are many sampling methods and types of sampling device capable of obtaining leachate and groundwater samples from boreholes all of which have their advantages and disadvantages. On some occasions it may be necessary to use separate devices for purging and sampling (e.g. a pump for removal of purge water followed by a bailer used for sampling). The following section provides information on the most common methods and devices currently in use under the following general headings:

* Bailers and depth samplers.
* Suction pumps.
* Inertial pumps.
* Electric submersible pumps and
* Gas displacement and bladder pumps.

### A10.3.2 Bailers and depth samplers

Bailers and depth samplers can be obtained for use in monitoring points over a wide range of diameters and can be constructed from a wide range of plastics or stainless steel. These devices provide a simple means of obtaining a “grab” sample either from the top of the water column (bailers) or from a specific depth in the water column (depth samplers). Both methods involve manually (or mechanically) lowering the sampling device into the borehole on a rope or wire and then withdrawing the device full of water to ground surface.

Bailers can also be used as a means of purging boreholes though this involves a great deal of physical effort and is less efficient than pumping methods.

Advantages and disadvantages are summarised in Table A10.1. For a more comprehensive discussion on bailers. For example, see Nielsen and Yeates (1985), MacPherson and Pankow (1988).

**Bailers**

Bailers are lowered to the water table where they are allowed to fill before being pulled back to the surface for sample recovery. Bailers are usually constructed from PVC, polypropylene, PTFE (Teflon) or stainless steel.

The bailer may be of varying levels of sophistication:

* Bucket type (open top, sealed base).
* Bottom check valve only. A ball and seat arrangement remains open during the sampler’s descent but closes under the weight of liquid in the sampler during removal.
* Double check valve bailer. Theoretically, both the upper and lower check valves close once the bailer stops descending through the water column, to collect a point specific sample. Double check-valve bailers allow depth sampling within the borehole.

**Table A10.1: Common types of borehole sampling equipment**

| **Equipment type** | **Description** | **Advantages** | **Disadvantages** |
| --- | --- | --- | --- |
| Depth samplers:  Bailers | Cylinder of appropriate diameter on rope or wire. Ideally filling through bottom check-valve. Can be PVC,  PTFE, stainless steel, or other material. | Low cost  Dedicated or disposable options Easy to operate  Readily portable. | Can only sample top of water column.  Low abstraction rate makes purging slow.  Causes agitation if operated too vigorously  Bailing cable a source of cross-contamination. |
| Depth samplers:  Discrete depth samplers | Container with closure at each  end – either a valve or a trigger mechanism. Lowered to required depth, sample, then withdraw. | Low cost – can be dedicated.  Fairly easy to operate.  Readily portable.  Can take depth profile of water column by sequential sampling. | Low abstraction rate makes purging slow.  Causes agitation if operated too vigorously.  Closures can fail, particularly when suspended solids present. |
| Pumps:  Electric submersible | Electrically powered positive displacement pumps, down to 50mm diameter. | 50mm dia pumps can operate to c.75 m depth. Larger diameter pumps will operate deeper.  Easy to operate.  Can be used for purging.  Can be used for low flow purging.1 | Need vehicular access for equipment (heavy)  Cause pressure changes and agitation.  Reduced capability in presence of suspended solids and higher temperatures. |
| Pumps:  Inertial | Length of tubing with foot valve. Oscillation causes water column to rise up tube. Can be  powered by hand or mechanically. | Low cost dedicated system Can operate to c.60m depth.2 Lightweight and portable mechanical unit available Simple field maintenance  Can operate in silty conditions.  Can be used for purging.2 | Can entrain suspended solids.  Causes agitation of sample. |
| Pumps:  Suction (including peristaltic) | Surface mounted pumps operating by suction exerted on water column. | Pump is at surface – dedicated tubing can be left in hole. Inertial pumps can be used as priming mechanism to avoid cross-contamination. | Can only operate to 7.6 m depth or less.  Suction degasses sample. Causes pressure changes and agitation.  May require priming, causing cross contamination. |
| Pumps:  Gas lift | Compressed air or gas provides positive pressure in sampler, driving sample to surface. | Can operate to any depth. | Gas comes into contact with sample, which may be degassed or subject to pressure changes.  Compressor/ tank must be taken to site. |
| Pumps:  Bladder | Compressed air or gas enters bladder in sampler, forcing sample to surface. Down to 50mm diameter. | Can operate to any depth.  Little sample disturbance.  Can be used for low flow purging. | Relatively expensive. Low abstraction rate makes purging difficult. |

1 Use of low flow rates can cause suspended solids to fall back down discharge line, causing blockage of the pump.

2 If operated mechanically.

**Discrete depth samplers – manually activated**

The simplest type of depth samplers are triggered via a weighted messenger clipped to the support line, allowing a sample to be grabbed from a predetermined point in the borehole. The bottom seal is often fitted with a valve and sampling tube to minimise aeration of the sample.

The advantages of this type of bailer are:

* Ability to sample at a preselected level in the borehole and
* Inexpensive.

The disadvantages are:

* Water passing through the tube as it travels downward may not be completely flushed out by the time it reaches the desired sampling level and
* The device may not seal completely in water containing suspended particles, (though this last problem is less frequent than it is with bottom check-valve bailers).

**Discrete depth samplers – mechanically activated**

Essentially these are the same as the manually activated systems with the exception that activation is either pneumatic or electrical. However, depth samplers such as these do provide a more representative sample than bailers while still being inexpensive, reliable and easy to maintain and operate. They are ideal for groundwater sampling for the analysis of general chemical parameters. Sequential sampling from the water surface to the bottom of the borehole is possible, enabling a profile of the water column to be measured.

### A10.3.3 Suction pumps

Suction-lift mechanisms are surface mounted pumps, either electrically, diesel or petrol powered. Due to the practical limit of suction lift of approximately 7.6 m (at sea level, reducing with altitude), this method of sampling is only practical for shallow water levels. The most commonly employed suction-lift pumps are the surface centrifugal pump and the peristaltic pump.

Advantages and disadvantages are summarised in Table A10.1.

**Surface centrifugal pumps**

The pump must first be primed by filling the impeller housing (self-priming). Water in the rotating impeller is discharged by a centrifugal force, which creates a partial vacuum, lifting water out of the borehole. These pumps are capable of very high delivery rates.

Suction pumps can be used readily for purging boreholes with shallow water levels, but there are several disadvantages to their use for sampling purposes:

* Degassing of volatile compounds through the negative pressure caused by the vacuum.
* Degassing through the action of the impeller, which imparts both a significant pressure change and a high degree of turbulence to the sample and
* Potential cross contamination from the priming water.

**Peristaltic pump**

These are self-priming, low-volume vacuum pumps consisting of a rotor and several ball bearing rollers within a pump head. Flexible tubing is squeezed by the rollers as they revolve around the rotor, creating suction. One end of the tubing, typically fitted with an intake strainer or screen, is placed into the borehole while the other is directed into a sample container. Only the tubing comes into direct contact with the sample. However, only silicone tubing has the flexibility to be used around the rollers and this is unsuitable for sampling some constituents (primarily organics) due to its adsorbing character.

Peristaltic pumps are particularly useful where samples have to be collected from narrow access tubes.

The biggest perceived disadvantage of a peristaltic pump is that it subjects water samples to negative pressures, which will affect the concentrations of dissolved gases and the pH of samples taken. Barker et al. (1987) suggest that volatilisation losses using suction-lift devices are insignificant relative to analytical and hydrogeological uncertainties.

### A10.3.4 Inertial pumps

Inertial pumps are comparatively cheap and suitable for a wide range of applications; their use as dedicated samplers is increasing.

The operating principle of the pump is based on the inertia of a column of water contained within a riser tubing. The pump consists of a foot valve connected by a rigid or semi-rigid rising main that runs to ground level. The whole system is alternately lifted and lowered at a rate sufficient to drive water continuously upwards to discharge at surface.

The pump can be operated manually at shallow depths, though is better used with a powered mechanical drive system to achieve greater lifts (e.g. to 60 m in a 50 mm diameter borehole).

The inertial pump is suitable for well development and purging and can operate in silty/sandy environments. Problems with the inertial pump arise from potential mixing of the water column in the casing caused by the up and down movements of the tubing and foot valve. However, experiments with dye have shown that mixing along the length of the casing is relatively insignificant compared to mixing across the diameter of the casing (Rannie and Nadon 1988). Other possible problems include agitation of the sampled water, and disturbance of accumulated sediment. With regard to the former, the pump has been tested for sampling volatile organics at depths of up to 8 m (Barker and Dickhout 1988), and in some instances performed better than a bladder pump. Placing the intake high in the water column, provided sufficient depth of water is available can reduce disturbance of sediment.

One of the main advantages of the inertial pump is that its drive mechanism and pump construction materials can be selected to suit a variety of technical and budgetary requirements. Its relatively low cost compared to other pumps and the fact that stiff tubing coils can make it difficult to transfer the pump between monitoring wells, make it more suitable for use as a dedicated pump in monitoring wells for both leachate and groundwater sampling.

Advantages and disadvantages are summarised in Table A10.1.

### A10.3.5 Electric submersible pumps

Electric submersible pumps operate by driving water upwards using helical rotors or gears.

Both types of pumps have an electric motor below the pumping mechanism, which draws in water under slight suction, then pressurises it for discharge. In the helical rotor pump, water enters the pump through a screened intake in the middle of the pump (above the electric motor) and is pushed upwards through a rotor-stator assembly. Water is transported to the surface through a discharge line. In the gear drive pump, the motor drives a set of two gears, which induce water through an intake screen at the top of the pump. Water is drawn through the gears and pushed in a continuous stream through a discharge port to a discharge line, which transports the water to the surface for sampling.

The inner workings of both types of pumps can be fabricated of inert or nearly inert materials. The only parts that should require replacement under normal field use are the two PTFE gears in the gear drive pump. With prolonged purging and/or sampling of water with high suspended solids, these gears may wear, resulting in diminished pump output. Water with a high suspended solids content can also cause operational problems in the helical rotor pump. High lift capabilities exist for deep-well applications (up to 600 m). From small diameter monitoring boreholes lifts are typically 50 m (for pumping from 50 or 75 mm diameter boreholes) to 100 m (for pumping from 100 mm diameter boreholes).

High pump rates may lead to the creation of turbulence and heat generation, especially in the helical rotor pump, which may cause alteration of sample chemistry. The potential for pressure changes (cavitation) exists at the drive mechanisms of the gear-drive pumps. Some pumps have temperature cut-out controls, which prevent their use in fluids (e.g. leachates) above the cut-off temperature.

Both types of pumps are highly portable and reliable to operate, except under silty conditions.

Advantages and disadvantages are summarised in Table A10.1.

### A10.3.6 Gas displacement and bladder pumps

Gas displacement and bladder pumps operate on the same principle, using hydrostatic pressure in the water to fill the pump chamber and compressed air to displace the water to the surface. Advantages and disadvantages are summarised in table A10.1.

**Gas-displacement pumps**

A wide variety of gas-displacement pumps are available, each with a slightly different design. The simplest type of device consists of a rigid cylindrical chamber, a screened intake, a bottom water-entry check valve, a gas-entry tube and a sample discharge tube, which are attached to the top of the cylinder. Both the gas-entry and sample discharge lines extend into the cylindrical chamber, with the sample discharge line extending almost to the bottom.

The pump is lowered to the required sampling depth and the system fills with groundwater. A positive gas pressure is applied for a fixed period through the gas entry tube to first close the bottom check valve and then force groundwater up the discharge line. After a fixed period has elapsed, the pressure within the system is dissipated. Groundwater within the rising main cannot return due to the check valve. After a pre-set period pressure is again applied, forcing water further up the rising main, this process continues until the sample is taken.

Flow rate from the system is optimised by adjusting the time over which pressure is applied and the interval over which the pump is allowed to refill with water. Where air pressure is applied properly, there is no contact between air and sample water and these devices can produce high quality samples, though usually at low yields.

Water samples can be collected by gas-displacement from virtually any depth (hundreds of metres), limited only by time availability, the burst strength of the tubing, the fittings and the sampling cylinder material (Nielson and Yeates 1985).

Gas-displacement devices can be used as portable or dedicated systems. In some circumstances they may even be installed in-situ within the borehole construction (For example, as a single buried installation or as a sampling device attached to a port on a multiple installation).

**Bladder pumps**

Gas-operated bladder pumps operate on the same principle as the gas-displacement pump, using hydrostatic pressure to fill the pump chamber and compressed air to displace the water to the surface. The primary difference in the bladder pump is the use of a flexible diaphragm or ‘bladder’ inside the pump chamber which isolates the water from the drive gas.

Their advantages include:

* Small diameter (may fit in 50 mm diameter boreholes).
* Pump can be constructed of inert materials.
* Little sample disturbance (therefore good for volatile compound sampling) and
* Models are available for pumping from depths in excess of 100 m.

These types of pumps only achieve relatively low discharge rates and are therefore utilised solely where low flow purging methods are suitable.

## A10.4 Surface water sampling equipment

Water samples are usually collected from surface watercourses using bailers or other transfer vessels before pouring water into sample containers. Where water is deep enough, sample containers can be filled directly within the watercourse. In some instances, pumps are used.

Specialist depth samplers can be used in deeper waters for obtaining a water sample at a specific depth or for collecting an integrated sample representative of the full depth of water.

Specialist methods are available for collection of sediment and biological samples from surface waters.

Sampling methods (including sediment and biological) and their advantages and disadvantages are described in detail in Standing Committee of Analysts, 1996.

## A10.5 Unsaturated zone sampling equipment

### A10.5.1 Introduction

Investigation of the unsaturated zone (vadose zone or zone of aeration) is an essential part of some environmental monitoring programmes as groundwater pollutants may be detected before reaching the groundwater table or saturated zone, thus providing an ‘early warning’ of potential groundwater pollution. The unsaturated zone is the geological profile extending from the ground surface to the water table in a water-bearing formation. Within the unsaturated zone, pore water is held in the rock matrix due to hydrostatic pressure.

Two types of devices are employed for sampling the ‘pore’ water: vacuum collection and free drainage collection:

* Suction samplers. Vacuum or suction devices (suction samplers) incorporate some type of porous material, which is placed in close contact with the soil and uses suction to collect the ‘pore’ water.
* Pan lysimeters. Free drainage, or zero-tension samplers (pan lysimeters) are placed within the soil profile, where they intercept and collect water percolating through the soil under the influence of gravity.

### A10.5.2 Suction samplers

Suction cup lysimeters are very simple devices consisting of a porous cup from which run two small bore tubes. When placed in the soil, the pores in these cups become an extension of the pore space of the soil. By applying a vacuum to the interior of the cup such that the pressure is slightly less inside the cup than in the soil solution, ‘pore’ water flow occurs into the cup. The sample is recovered at ground level through application of a vacuum or positive pressure (deep installations) to the sampler.

Suction samplers may be subdivided into two categories, depending on the depth at which they are installed and therefore the method of bringing the sample to the surface. Vacuum or vacuum-pressure operated suction samplers are used when the solid depth is less than or greater than 1.8 m respectively.

Suction cup lysimeters are easy to install, are relatively inexpensive and can be installed without causing extensive disturbance to surrounding soil or structures. However, there are several problems which can limit their effectiveness. Suction lysimeters are point samplers, and because of the small volume of sample obtained, the representativeness of the results is questionable. The water sampled is in ‘blocks’. In structured soils, water moving through cracks may have different ionic composition than water in blocks. The suction applied may affect soil-water flow patterns. Tension meters should be installed to ensure that the proper vacuum is applied. The porous segments may become clogged, and water collected in the ‘dead-space’ of a lysimeter (areas from where simple water is unable to be removed) may contaminate future samples. For comprehensive discussions of the limitations of suction-cup lysimeters; for example see Everett et al. 1988, and Hornby et al. 1986.

Torstensson 1984 describes a modification to the basic suction-cup lysimeters that alleviates some of the problems associated with gas drive devices mentioned above. Practical operating depths range up to 60 m.

### A10.5.3 Pan lysimeters

The pan lysimeter, which is a free-drainage type lysimeter, has been designed to study the constituents of gravitational water percolating through the unsaturated soil in situ, i.e. macropore or fracture flow in highly structured soils.

There are a number of designs for pan-type lysimeters (e.g. Hornby et al. 1986) and they can be constructed of any non-porous material, provided a leachate (water sample) / pan interaction will not jeopardise the validity of the monitoring objectives. The pan itself may be thought of as a shallow-draft funnel. Water draining freely through the macropores will collect in the soil just above the pan cavity. When the tension in the collecting water reaches zero, dripping will initiate and the pan will funnel the leachate into a sampling bottle. Fine sand packing or the use of a tension plate reduces capillary tension at the cavity face and promotes free water flow into the pan.

The installation of pan-lysimeters varies, but the most common methods are the trench and trench and tunnel techniques. The trench method can introduce a sampling bias, because if the pan lysimeter is installed close to the trench wall, the trench shelter will cause waste application equipment to avoid the actual sampling area to avoid damage to the shelter. Hence any leachate generation will tend to occur away from the sampling areas. The trench and tunnel method has been designed to overcome this problem. A pan lysimeter is installed into the sidewall of a trench and connected to a remote point at the surface via a discharge line. The distance between the lysimeter and the discharge point should be at least 10 m to preclude any sampling bias above the lysimeter. When a sample is required, a vacuum is placed on the discharge line and a sample is retrieved. After the sampling lines are installed, the lysimeter installation trench is backfilled. This method only allows monitoring in the soil to a depth of 1.5 m and has limited application for monitoring existing facilities, such as landfills (Hornby et al. 1986).

Pan lysimetry is a continuous sample collection system without the need for an externally applied vacuum. Because a vacuum is only used to pull the sample to the surface, there is less potential for losing volatile compounds in the sample obtained. Its defined surface area may allow quantitative estimates of leachate and the method of installation allows for monitoring the natural percolation of liquids through the unsaturated zone without alteration of flow.

## References

Barcelona, M.J. and Gibb, J.P. (1988). *Development of effective groundwater sampling protocols*. In: Groundwater contamination: field methods, edited by Collins, A.G. and Johnson, A.I., 17-26. ASTM. USA.

Barcelona, M.J. and Helfrich, J.A. (1986). *Well construction and purging effects on groundwater samples*. Environmental Science and Technology, 20, 11, 1179-1184.

Barcelona, M.J., Helfrich, J.A., and Garske, E.E. (1988). *Verification of sampling methods and selection of materials for groundwater contamination*. In: Groundwater contamination: field methods, edited by Collins, A.G. and Johnson, A.I., 221-231. ASTM. USA.

Barcelona, M.J., Helfrich, J.A., Garske, E.E., and Gibb, J.P. (1984). *A laboratory evaluation of groundwater sampling mechanisms*. Ground Water Monitoring Review, 4, 2, 32-41.

Barker, J.F. and Dickhout, R. (1988). *An evaluation of some systems for sampling gas-charged ground water for volatile organic analysis*. Ground Water Monitoring Review, 8, 4, 112-120.

Barker, J.F., Patrick, G.C., Lemon, L., and Travis, G.M. (1987). *Some biases in sampling multilevel piezometers for volatile organics*. Ground Water Monitoring Review, 7, 2, 48-54.

Barvenik, M.J. and Cadwgan, R.M. (1983). *Multilevel gas-drive sampling of deep fractured rock aquifers in Virginia*. Ground Water Monitoring Review, 3, 4, 34-40.

Bishop, P.K., Burston, M.W., Chen, T., and Lerner, D.N. (1991). *A low cost dedicated multi-level groundwater sampling system*. Quarterly Journal of Engineering Geology, 24, 311-321.

Church, P.E. and Granato, G.E. (1996). *Bias in groundwater data caused by well-bore flow in longscreen wells*. Ground Water, 34, 2, 262-273.

Clark, L. (1988). *The field guide to water wells and boreholes*. Geological Society of London Professional Handbook. Open University Press. Milton Keynes ISBN: 0-335-15203-1.

Clark, L. and Baxter, K.M. (1989). *Groundwater sampling techniques for organic micropollutants: UK experience*. Quarterly Journal of Engineering Geology, 22, 159-168.

Everett, L.G., McMillon, L.G., and Eccles, L.A. (1988). *Suction lysimeter operation at hazardous waste sites*. Ground water contamination: field methods, ASTM STP 963, edited by Collins, A.G. and Johnson, A.I., American Society for Testing and Materials. 304-327

Gibs, J., Brown, G., Turner, K.S., Macleod, C.L., Jelinski, J.C., and Koehnlein, S.A. (1993). *Effects of small-scale vertical variations in well-screen inflow rates and concentrations of organic compounds on the collection of representative ground-water-quality samples*. Ground Water, 31, 2, 201-208.

Hornby, W.J., Zabcik, J.D., and Crawley, W. (1986). *Factors which affect soil-pore liquid: a comparison of currently available samplers with two new designs*. Ground Water Monitoring Review, 6, 2, 61-66.

Hutchins, S.R. and Acree, S.D. (2000). *Ground water sampling bias observed in shallow conventional wells*. Ground Water Monitoring Review, Winter 2000, 86-93.

Johnson, T.L. (1983). *A comparison of well nests vs. single-well completions*. Ground Water Monitoring Review, 3, 1, 76-78.

MacPherson, J.R.J. and Pankow, J.F. (1988). *A discrete point sampler for ground water monitoring wells*. Ground Water Monitoring Review, 8, 3, 161-164.

Nielsen, D.M. and Yeates, G.L. (1985). *A comparison of sampling mechanisms available for small diameter monitoring wells*. Ground Water Monitoring Review, 5, 2.

Patton, F.D. and Smith, H.R. (1988). *Design considerations and the quality of data from multiple level ground-water monitoring wells*. in: Collins, A.G. and Johnson, A. I., Editors. Ground-Water contamination: Field methods, ASTM STP 963. Philadelphia, USA. American Society for Testing and Materials. pp. 206-217.

Rannie, E.H. and Nadon, R.L. (1988). *An inexpensive, multi-use, dedicated pump for ground water monitoring wells*. Ground Water Monitoring Review, 8, 4, 100-107.

Robin, M.J.L. and Gillham, R.W. (1987). *Field evaluation of well purging procedures*. Ground Water Monitoring Review, 7, 4, 85-93.

Standing Committee of Analysts (1996). *General principles of sampling waters and associated materials (second edition); Estimation of flow and load*. Methods for the examination of waters and associated materials. HMSO. UK ISBN: 0 11 752364 X.

Torstensson, B.A. (1984). *A new system for groundwater monitoring*. Ground Water Monitoring Review, 4, 4, 131-138.

# Appendix 11: Quality Control Sampling

## A11.1 Introduction

### A11.1.1 Context of Quality Control Sampling

Two types of procedure used for Quality Control are:

* Error minimisation, achieved by standardised good practice in data collection and handling and
* Error detection, achieved by measuring and checking for errors.

Error detection itself consists of two components:

* Quality control sampling. The collection of samples for the specific purpose of measuring errors. The subject of this appendix and
* Data validation. The checking of monitoring data for errors. This includes consideration of the errors measured by quality control sampling. Data validation is dealt with in a separate appendix.

From the above it will be clear that quality control sampling (QC sampling) is a necessary part of overall Quality Control effort.

### A11.1.2 QC sampling strategy

The initial main quality control sampling effort will be directed at determining the overall contribution to variability made by sampling and analytical errors (as opposed to real variation in the water body). If the contribution made by errors is unacceptable in terms of the tolerable uncertainty for a particular determination, it will then be necessary to carry out further QC sampling in order to determine the main sources of the errors.

A study of the sampling, handling and analysis methods in use may direct attention to suspected sources of error, and it is then possible to select QC sampling techniques to target these.

### A11.2 Types of QC sample

Table A11.1 describes a number of types of QC sample, classified in relation to the overall sampling and analysis process. At each point in the process (see left hand column of Table A11.1) it is possible to take QC samples, and these samples will provide an indication of variability introduced by all subsequent parts of the process. The later in the process a QC sample is taken, the more precisely the source of error is determined. The earlier in the process a QC sample is taken, the more sources of error are taken into account. Initially QC samples should be taken as near the start of the process as possible, and if the errors detected are acceptable, then no further action is required. If the errors detected are unacceptable, then further QC samples should be taken at other points in the process to detect the sources of error.

QC samples obtained by splitting a sample (duplicates) can only detect random errors (which affect precision). Systematic errors (which cause bias) can only be detected by blanks and standards/ spikes. Blanks can only detect gains in a determination (For example, due to cross contamination or desorption), while standards and spikes can detect gains and losses (For example, due to precipitation, adsorption, degassing). Thus the greatest amount of QC information is provided by a standard or spiked sample, and the least by a duplicate sample. Table A11.2 summarises the advantages and disadvantages of these three generic types of QC sample.

**Table 11.1a: Types of quality control sample for sampling quality control**

| **QC Sample location** | **Duplicate QC Sample** | **Blank QC Samples** | **Standard / spiked QC Samples** | **Errors or variability detected** |
| --- | --- | --- | --- | --- |
| 1. Water body | Sampling duplicate (i.e. repeat entire sampling procedure) | (not possible) | (not possible) | Total of: Purging/ short term natural variability, plus errors below. |
| 1. Sampling equipment | Equipment duplicate (i.e. repeat use of sampling equipment) | Equipment field blank1 | Equipment field standard/ spike1 | Total of: Sampling equipment/ some short term natural variability (in the case of duplicate), plus errors below. |
| 1. Prior to treatment (e.g. filtering/ preservation) | Prior to treatment (e.g. filtering/ preservation) | Pre-treatment duplicate (split sample prior to treatment, then treat both samples identically) | Pre-treatment field blank | Pre-treatment field standard/ spike |
| 1. Prior to bottling | Post-treatment duplicate | Post-treatment field blank | Post-treatment field standard/ spike | Total of: Ambient conditions, plus errors below. |
| 1. Prior to transport | (not possible) | Trip blank | Trip standard/ spike | Total of: Handling and transport, plus errors below. |
| 1. Sample bottles | (not possible) | Bottle blank (i.e. place deionised water in bottle and submit for analysis) | Bottle standard/ spike (i.e. place standard or spiked sample in bottle and submit for analysis) | Total of: Bottle material and preparation, plus errors below. |
| 1. Delivery to laboratory | Lab duplicate | Lab blank | Lab standard/ spike | Total laboratory errors1. |

1 Only possible if equipment is removable. For dedicated sampling equipment, this QC sample becomes less important. NB: This table only relates to the sampling process. Further QC samples should be prepared in the laboratory, in order to detect errors during the laboratory handling and analytical process.

**Table 11.1b: Types of quality control sample for sampling quality control**

|  |  |
| --- | --- |
| **Type of errors detected** |  |
| **Random only** |  |
| **Random and systematic gains only** |  |
| **Random and systematic gains and loses** |  |

**Table 11.2: Comparison of duplicate, blank and standard/spike samples**

| **QC sample type** | **Advantages** | **Disadvantages** |
| --- | --- | --- |
| Duplicate | * Sampling process itself can be duplicated (sampling duplicate), providing information on errors in the entire sampling/ analysis process; * Relatively easily performed; and * Can be applied for all determinands. | * Only detects random errors; systematic errors are not detected. |
| Blank | * Easily performed; * Can be applied to all determinands; and * Detects some random and systematic errors. | * Cannot be applied to initial sampling; and * Only detects gains in determinand; losses are not detected. |
| Standard/ spike | * Detects all random and systematic errors from point of QC sampling. | * Requires laboratory prepared standard solution. Can be more difficult to perform; and * Each sample usually applies to only one determinand. |

## A11.3 Processing of QC samples and data

### A11.3.1 QC sample handling

QC samples should be handled in exactly the same way as normal samples. Care should be taken to achieve and record this.

Duplicate and blank samples should be labelled in such a way as to be indistinguishable from normal samples by the laboratory.

### A11.3.2 Data handling

Results of all QC analyses should be interpreted and archived separately from normal results, although a record of results of duplicate analyses may also be processed with normal results.

All QC results should be referenced to their relevant monitoring results. For example, a trip sample may refer to all samples on a trip, while a sampling duplicate may refer to a single sample. In this manner, doubt arising from QC breaches will be referenced to the appropriate monitoring results.

The interpretation of QC sample results is covered in Appendix 13.

# Appendix 12: Laboratory Analysis

## A12.1 Preamble

This appendix provides guidance covering:

* Sample handling and preparation.
* Analytical techniques.
* Laboratory quality assurance and quality control and
* Laboratory documentation and reporting.

## A12.2 Sample handling and preparation

The handling and preparation of samples, from the moment of delivery to postanalytical storage and final disposal, forms a vital part of the laboratory operation. These factors can have as much effect on data quality as the analytical techniques themselves. Furthermore, as these aspects of the operation are sometimes outside the scope of accreditation or quality schemes, it is important for laboratory users to obtain clarification on how quality is achieved in these areas.

Table A12.1 is a checklist which can be used to assess these aspects.

## A12.3 Specification of analytical methods

Standard methods of analysis are available for many of the determinations required routinely by landfill monitoring. Typical specifications used by UK laboratories include:

* Standing Committee of Analysts (SCA) ‘Methods for the Examination of Water and Associated Materials’ (referred to as the “Blue Book”).
* American Society for Testing of Materials (ASTM) and
* United States Environmental Protection Authority (USEPA).

Laboratories also commonly use variations on these standards, or methods developed in-house. This is particularly true for inorganic analysis of contaminated water samples, and for determinations of compound groups such as mineral oils and phenols. Where in-house procedures are adopted, these should be documented to the same extent as the standard methods. Where it is required to compare data from different laboratories it is preferable to use standard methods or, as a second best, include comparison with standard methods in the documentation.

**Table 12.1: Checklist assessment of laboratory sample handling aspects**

**Table 12.1a: Reception / registration**

| **Item** | **Check** |
| --- | --- |
| Are all samples delivered during working hours unpacked and sent for analysis/ preservation on day of delivery? |  |
| Are satisfactory arrangements in place for out of hours delivery if required? |  |
| Is the client notified of sample receipt and analysis schedule? |  |
| Is the client allocated a single contact person for the job? |  |

**Table 12.1b: Preservation / storage of main sample**

| **Item** | **Check** |
| --- | --- |
| Does the lab have a cool room of sufficient size for the throughput of the lab? |  |
| Is the cool room temperature controlled at close to 4°C? |  |
| Is main sample stored in cool dark conditions following sub-sampling and analysis for an agreed acceptable period (min 1 month)? |  |

**Table 12.1c: Segregation**

| **Item** | **Check** |
| --- | --- |
| Does analysis request form include information on sample matrix and degree of contamination? |  |
| Are water samples segregated from soil samples? |  |
| Are ‘clean’ samples (e.g. uncontaminated groundwater or surface water) segregated from ‘dirty’ samples (e.g. sewage, leachate)? |  |
| Are samples segregated by speed of analysis required? |  |

**Table 12.1d: Preparation**

| **Item** | **Check** |
| --- | --- |
| Are special requests for preparation/ sub-sampling taken account of (e.g. sub-sampling from shaken or settled sample/ use of special filter size)? |  |
| Is preparation carried out immediately where required (e.g. preparation of filtered preserved sub-sample for trace metals analysis)? |  |
| Is the sample routinely homogenised before sub-sampling? |  |
| Where filtration is required, is the size and type of filter used appropriate for the analysis, and reported with the result? |  |
| Is an acceptable method used for preparation/ sub-sampling of samples with high suspended solids content? |  |
| Where solvent extraction is required, is the method appropriate and are quality control checks run with similar samples to enable accurate estimation of recovery rates? |  |

**Table 12.1e: Scheduling and records**

| **Item** | **Check** |
| --- | --- |
| Is sample ID transferred to sub-samples in a permanent, auditable manner? |  |
| Are procedures scheduled well within technical time limits? (examples of procedures with short time limits include preservation, solvent extraction, pH determination, and analyses for BOD, nitrate, nitrite, orthophosphate and hexavalent chromium). |  |
| For time-critical procedures, is the time recorded and reported? |  |
| If field treatment has been carried out (e.g. filtration/ preservation) can this be included in the record? |  |

**Table 12.1f: Disposal**

| **Item** | **Check** |
| --- | --- |
| Is the period of storage after analysis sufficient?  Are samples disposed of to an appropriate licensed facility? |  |

All methods (whether standard or in-house) require validation in the laboratory concerned, for the sample types concerned. Validation requires evaluation of the following:

* Precision.
* Accuracy.
* Overall uncertainty.
* Limits of detection.
* Applicability.
* Interferences and
* Traceability to national standards.

Once validated, continued performance of the method should be maintained and demonstrated through quality control and proficiency testing (see next section).

The laboratory analyst should select the most appropriate method of analysis on the basis of information supplied by the client. This information should include the following:

* Determination required. (e.g. individual element, individual compound, total of a group of compounds, scan for a range of substances).
* Type of sample. (e.g. leachate/ groundwater/ pond water).
* Likely concentration range.
* Maximum acceptable minimum reporting value. (derived from likely concentration range and, where applicable, assessment limit e.g. minimum reporting values for List I substances).
* Maximum acceptable total laboratory error on a single result. (derived from tolerable uncertainty, making allowance for errors already introduced by the sampling and handling process).
* Possible hazards associated with the samples and
* Required turnaround time.

For simpler determinations a single standard method will achieve most users requirements and there will be little discussion of appropriate technique. In other cases a choice must be made between two or more methods, or a decision taken to modify a standard method. Examples for determinands commonly monitored at landfills include the following:

* Metals determinations. Metals are often analysed by ICP-AES[[23]](#footnote-23) (particularly when more than 5 metals are to be determined, as the method allows simultaneous determination). However, the method has a high uncertainty for sodium and potassium, can be affected by interference between cations and from organics, and has limits of detection which are high in relation to drinking water limits for some trace metals (e.g. lead and cadmium). Other techniques such as AAS[[24]](#footnote-24) or ICP-MS[[25]](#footnote-25) may be applicable depending on the metals and minimum reporting limits required.

‘Dissolved metals’ determinations are also affected by filter type and pore size.

* Ammoniacal nitrogen. Determination by ion specific electrode or colourimetric method allows low cost analysis but with detection limits which are quite high in relation to the drinking water standard. The methods are also susceptible to interference. Ion chromatography offers lower limits of detection and less interference problems.

Method and time of preservation will also affect this determination.

* Bicarbonate. Often calculated from a determination of alkalinity. However in samples with significant concentrations of ammonia and/or organic acids, this will be in error. If bicarbonate concentration is required for its own sake or as a quality control check, an alternative method such as high temperature catalytic oxidation could be used for leachate and other contaminated samples.
* COD, BOD, TOC. These determinations are affected by filter type and pore size.

BOD suffers from poor precision and dilution effects.

TOC determination can involve an initial purging process which results in loss of volatile compounds. A method should be chosen that is appropriate for the sample and information required.

* Organic compounds. Determination frequently involves solvent extraction as a first step. The solvent used and the extraction method will affect the result. It is not possible to specify a ‘best’ extraction method, as different methods are more efficient for different analytes and matrices. Whichever method is used, a bias will be introduced by the extraction process, which the laboratory must correct. It is important to check whether the corrections used apply to the type of sample being analysed.
* Mineral oil. ‘Mineral oil’ is a term without a precise definition, and it is therefore particularly important to specify the method used and report this with the result. For example, determination by Infra-Red will detect straight-chain hydrocarbons found in lube oil and diesel but will miss many of the compounds found in petrol. Other methods, such as determination of specific carbon ranges by GCFID[[26]](#footnote-26), will yield different results, and an appropriate method should be specified in consultation between operator, SEPA and laboratory and
* Phenols. Phenols are a complex group of compounds and some tests will only detect selected types of phenol.

Laboratories often make detection limits for determinations readily available to assist in decision making. Data on uncertainty (precision and accuracy) and applicability to different sample types are not so readily available but can be equally important when considering the selection of appropriate analytical methods.

The choice of analytical method could affect field procedures. Where appropriate, sampling protocols should be modified to ensure the analytical method is as reliable as it needs to be (e.g. the need or otherwise for field filtration and preservation, or the provision of additional volume of sample required to allow duplicate analyses).

## A12.4 Laboratory quality control

When selecting an analytical laboratory, evidence of effective quality control should be sought. As well as method validation (see previous section) a typical range of schemes operated by any reputable laboratory would include the following:

* Internal calibration and quality control checks. All analytical methods undertaken should be subject to routine calibration and quality control checks. These will include the regular running of blanks, standards (including external standards) and spiked samples to enable estimation of accuracy and precision. Control charts should be used to provide assurance of performance. It is important that standards and spiked samples are run for relevant concentration ranges and sample types. For example, accuracy and precision may be within acceptable limits for clean water samples but unknown (and possibly unacceptable) for leachates.

Analytical results should be subject to audit checks prior to reporting. All calculations undertaken should be accessible to external scrutiny. Any reputable laboratory will be able to produce quality control and audit records on request.

* External analytical comparison checks. Laboratories may voluntarily participate in comparative analytical checking schemes such as ‘Aquacheck’[[27]](#footnote-27) or ‘LEAP’[[28]](#footnote-28). Checks cover a limited range of analyses and may not necessarily cover every analyte specified in monitoring schedules. Checks may only be undertaken on “clean” water samples rather than more analytically difficult “dirty” water samples such as leachates. Laboratories should be prepared to demonstrate satisfactory performance for different types of water and
* Third party accreditation checks. Voluntary participation in quality assessment schemes such as that operated by the United Kingdom Accreditation Service (UKAS) provide independent certification of standards and quality control procedures operated by a laboratory, including adoption of appropriate written and chain of custody records. UKAS accreditation itself does not guarantee accuracy of analyses but does require laboratories to participate in recognised external check sampling schemes.

Some laboratories subcontract work to other laboratories. In this situation it is important to establish that accountability remains with the main laboratory, and that appropriate quality control measures are in place both for the analyses concerned and for the sample handling involved.

## A12.5 Laboratory reporting

The ‘product’ of a laboratory is its reports, so the effort exerted for analytical quality control should also apply to the compilation of data and reports. The laboratory should undertake routine checks for transcription errors, and preliminary validation checks on data (such as ion balance calculation) to enable early detection of possible analytical errors.

A laboratory report should include the following information:

* Sample identification.
* Dates when samples were delivered, analysed and reported.
* Results of determinations.
* Units of measurement.
* Minimum reporting limits.
* Uncertainty in laboratory measurement. As a minimum, analytical precision should be reported. Data on overall uncertainty (accuracy and precision) should be available on request.
* Analytical method used. This may be a simple abbreviation, but a fuller description should be available on request.
* Comments or summary of sample preparation procedures. e.g. type and pore size of filter use, digestion and/or mixing method.
* Laboratory quality control report. For routine analyses this may consist simply of a check box. Full QC data should be available on request.
* Analyst’s comments. e.g. problems with sample, reasons for non-reporting of analyses, ion balance outside specified range and
* Analyst’s certification.

The scheduling and format of reports may be specified in a contract with a laboratory. For example, a mechanism is needed to distinguish preliminary results from final validated results, and client checking of preliminary results needs to be scheduled within a reporting scheme.

Report format may be paper-based or electronic, or both. If both, then it should be agreed which is the ‘master’ version. There are a number of standard reporting formats available, particularly for electronic reporting. Many database systems adopt their own proprietary standards. Others, such as the Association of Geotechnical and Geoenvironmental Specialists (AGS) are freely available to institutional members.

There is as yet no established UK standard format for environmental data.

# Appendix 13: Data Validation

## A13.1 Introduction

This appendix is concerned with the detection of errors in monitoring data. Details are given of a number of checks that should be made on monitoring data, in order to:

* Provide confidence in its validity and
* Direct attention to sources of error, so that corrective action can be taken.

Different types of data require different types of check. For example,:

* Water level or flow data. Checked for consistency mathematically and against historical records.
* Inorganic chemical data. Checked using rules derived from an understanding of the chemistry of aqueous solutions and
* Organic analyses. Checked using comprehensive quality control sampling procedures. (Organic analytes are often at trace concentrations and capable of being strongly affected by sampling and handling).

This appendix consists of the following subsections:

* A13.2 Monitoring data.
* A13.3 Data validation.
* A13.4 Validation of water level and flow data.
* A13.5 Validation of water chemistry data.
* A13.6 Validation of biological data and
* A13.7 Automation of data validation.

## A13.2 Monitoring data

Table A13.1 shows a typical range of data types arising from a water monitoring programme at a landfill. Some of the data (e.g. monitoring point details) remain constant over a period of time and are best tabulated or filed separately. This data is designated as ‘relational’ or ‘meta’-data, while other data is time dependent and is entered into the core data tables or files.

**Table A13.1: Example of data types arising from water monitoring programme**

| **Data** | **‘Relational’ data?** | **Data type1** | **Internal consistency check required?2** |
| --- | --- | --- | --- |
| Site details | Y | Text/ numeric |  |
| Monitoring point details | Y | Text/ numeric |  |
| Laboratory analyses |  | Numeric, censored | Y |
| Field quality measurements |  | Numeric, censored | Y |
| Field notes/ sample history report |  | Text/ logical |  |
| Detection limits | Y | Numeric |  |
| Margins of error | Y | Numeric |  |
| Analysis method | Y | Text |  |
| Field QC sample analysis results |  | Numeric, censored | Y |
| Lab QC results |  | Numeric, censored | Y |
| Data corrections (QC) |  | Numeric |  |
| Remarks (e.g. sampler's, analyst's or data reviewer's comments) |  | Text |  |
| Water/ leachate level/ flow data |  | Numeric | Y |
| Other data (e.g. landfill gas) |  | Numeric/ text/ logical |  |
| User inputs (e.g. validation rules, threshold limits, conversion factors) | (Y) | Numeric/ text/ logical |  |
| Records of data audits |  | Text/ logical |  |

1 Data may generally be classified as numeric (including date/ time data), textual, or logical (Boolean, i.e. true/ false). Numeric data may be censored (i.e. values above or below a limit reported as ‘less than’ or ‘greater than’ the limit).

2 See Section A13.3 ‘Data Validation’, below.

Both relational and core data are required at the time of data validation.

It is often not possible to enter all data into a single storage system, unless the system is paper-based or the electronic system is entirely in text format. Accordingly, the raw data will contain information not held elsewhere. Raw data forms the primary information source of any data set and should be maintained in an available form to enable data validation checks to be made at any time in the future.

## A13.3 Data validation

Data should be subjected to ‘internal’ consistency checks and ‘external’ checks against other related data.

### A13.3.1 Internal checks

Data should be checked for:

* Simple errors (e.g. missing data, misnumbering, transcription errors).
* Logical errors (e.g. data outside valid ranges) and
* Technical inconsistencies.

### A13.3.2 External checks

The data must also be checked externally against:

* Field measurements.
* Simultaneous analyses from relevant nearby sampling points.
* Previous analyses from the same sampling points.
* Results from QC sample analyses and
* Sample ‘attributes’ (i.e. adherence to sampling / handling protocols, unusual conditions).

In the following subsections, checks are described for different types of monitoring data.

## A13.4 Validation of water level and flow data

### A13.4.1 Internal checks

* Monitor point identification. Especially important with multiple or clustered monitor points or where monitoring points have been renumbered.
* Missing data. For example, data should be recorded on surface water bodies that are dry, or boreholes that are dry or blocked or damaged (depth to base should be included in the record).
* Transcription errors. A proportion (5-10%) of data should be compared against raw data, to ensure transcription errors have not been introduced during copying or validation routines.
* Data outside valid range. For example, levels which are below base or above top of a borehole or water body and
* Technical inconsistencies. For example, level data not correctly reduced to Ordnance Datum (e.g. due to datum point movement), or computational errors in the calculation of flow from staff gauge readings.

### A13.4.2 External checks

* Equipment calibration records. For example, water level dip tape accuracy (especially for repaired tapes). Flow measuring equipment calibration.
* Field notes. Check for any record of unusual conditions which may influence dip measurements (e.g. damaged or new headworks) and
* Comparison with previous and adjacent records. Where data diverges from a known trend, or from a correlation with other similar data records, an explanation should be sought.

## A13.5 Validation of water chemistry data

### A13.5.1 Internal checks – general methods

* Monitor point identification. Especially important with multiple or clustered monitor points or where monitoring points have been renumbered.
* Missing data. Sample analysis request forms should be checked against returned data.
* Transcription errors. A proportion (5-10%) of data should be compared against raw data, to ensure transcription errors have not been introduced during copying or validation routines.
* Data outside valid range. Valid ranges can be based on detection limits of analyses, or logical limits (e.g. positive value only). In some instances checks based on determinand properties may be used (e.g. maximum solubilities) and
* Incompatible constituents. Certain constituents can only exist in solution (in steady state) under particular pH or redox conditions. If the sample is in equilibrium, indicators of differing conditions should not occur in the same sample. For example, many metals have low solubility at moderate pH values; indicators of oxidising conditions (e.g. dissolved oxygen) would not be expected with indicators of reducing conditions (e.g. ammonia).

### A13.5.2 Internal checks – major ion balance

Calculation of the ionic balance for dissolved ions in a water sample is a convenient check on the internal consistency of major ions in a laboratory analysis - but only where sufficient major ions have been analysed to enable this check to be carried out. An ionic balance does not provide any information on the reliability of any other chemical constituents (e.g. organics or minor inorganics).

Where laboratories quote major ion balances, it is important to confirm that all analyses used in the calculation have been carried out by analytical means and not determined by back-calculation to achieve a perfect balance.

An ion balance calculation compares the sum of the main cations and anions as milliequivalents/litre (meq/l). The formula for conversion of mg/l concentrations into meq/l concentrations is as follows:





Table A13.2 gives charges and molecular weights for the common major ions and some ions more commonly found in contaminated waters and leachates. The fifth column gives the factor (charge / molecular weight) which can be multiplied directly by the concentration in mg/l to give the equivalent concentration. Care must be taken to ensure that the molecular weight used is appropriate for the ion as reported. (For instance, a nitrate concentration reported as nitrogen must be divided by the weight of nitrogen not nitrate. Both factors are provided in Table A13.2.) The formula for calculation of ion balance is:



For **uncontaminated waters**, ion balance can generally be calculated using major ions only (ignoring ‘contaminant’ ions, see Table A13.2). **In these waters ion balance should be within ±5%**.

(Note that some authors/ laboratories calculate ion balance as a proportion of total cations (or anions) only, rather than the sum of anions and cations. It may also be calculated as a proportion of the average of cations and anions, which is the most logical method, but rarely used. In both these cases the percentage ion balance would be twice that produced from the above equation).

**Table 13.2a: Charges and molecular weights for common major ions and some ‘contaminant’ ions – Cations (+ charge)**

| **Ion** | **Major / Contam.** | **Charge** | **Molecular weight** | **Charge mol. wt.** |
| --- | --- | --- | --- | --- |
| Calcium (as Ca) | M | 2 | 40.08 | 0.0499 |
| Magnesium (as Mg) | M | 2 | 24.32 | 0.0822 |
| Sodium (as Na) | M | 1 | 22.99 | 0.0435 |
| Potassium (as K) | M | 1 | 39.09 | 0.0256 |
| Iron (as Fe2+) | C | 2 | 55.85 | 0.0358 |
| Manganese (as Mn) | C | 2 | 54.94 | 0.0364 |
| Ammoniacal nitrogen (as N)1 | C | 1 | 14.01 | 0.0714 |
| Ammoniacal nitrogen (as NH4)1 | C | 1 | 18.04 | 0.0554 |

1 This value is actually the sum of two species: ammonium and dissolved ammonia. The latter is not an ion and should not theoretically be included in the ionic balance. However, in practice it may be included because dissolved ammonia also affects the alkalinity value and the two effects cancel each other.

**Table 13.2b: Charges and molecular weights for common major ions and some ‘contaminant’ ions – Anions (- charge)**

| **Ion** | **Major / Contam.** | **Charge** | **Molecular weight** | **Charge mol. wt.** |
| --- | --- | --- | --- | --- |
| Chloride (as Cl) | M | 1 | 35.45 | 0.0282 |
| Sulphate (as SO4) | M | 2 | 96.06 | 0.0208 |
| Nitrate (as NO3) | C | 1 | 62.01 | 0.0161 |
| Nitrite (as NO2) | C | 1 | 46.01 | 0.0217 |
| Nitrate or Nitrite (as N) | C | 1 | 14.01 | 0.0714 |
| Alkalinity (as CaCO3)2 | M | 2 | 100.09 | 0.0200 |
| Alkalinity2 or bicarbonate (as HCO3) | M | 1 | 61.02 | 0.0164 |
| Phosphate (as P)3 | C | 3 | 30.97 | 0.0323 |
| Phosphate (as PO4)3 | C | 3 | 94.97 | 0.0316 |

2 Assumes alkalinity is caused entirely by bicarbonate/ carbonate (but see note 1 above).

3 Assumes all phosphate present as orthophosphate.

An excessive ion imbalance indicates one of two effects:

* The water contains ions which have not been included in the calculation. In some uncontaminated waters (particularly groundwaters) other ions (e.g. iron, nitrate, borates, silicates and phosphates) may be present in sufficient quantity to merit inclusion in the ionic balance. In leachates and leachate contaminated waters all the contaminant ions in Table A13.2 above should be included when calculating the ionic balance though other effects may also need to be considered (see below) and
* Errors have been introduced during the analytical procedure. These may be due to analytical errors, or due to real changes in the sample or subsamples during the analytical process. In either case the poor ion balance implies uncertainty in the analytical results.

As stated in the first bullet point above, leachates and leachate contaminated waters present additional issues for consideration before a poor ion balance can be attributed to poor laboratory QC. In particular:

* Carboxylic acids (‘fatty acids’ such as ethanoic , propanoic and n-butanoic acids) are commonly present in leachate in biodegradable landfills. These compounds are described as ‘weak’ acids, meaning they are present partly in a ‘combined’ non-ionic form and partly in ionic form. To the extent that they are ionic, they will contribute to the ion balance.
* The presence of carboxylic acids also has an interference effect on the measured value of alkalinity. A correction can be made for the combination of this effect and the previous one, provided that pH and alkalinity have been measured accurately as soon as possible after sampling, and the concentrations of relevant carboxylic acids have been measured.
* Dissolved ammonia converts to ammonium ions as the pH is reduced during the alkalinity titration. This also affects the alkalinity measurement. This effect should be cancelled out in the ion balance calculation by the inclusion of ammonia in the cation total and
* The presence of oxidisable or hydrolysable ions (e.g. ferrous/ferric iron, manganese and aluminium) can also contribute to alkalinity and may need compensation.

Many of the above complications surround the measurement of alkalinity. If ionic balance problems are experienced with leachates and leachate contaminated waters it may be appropriate to avoid dependence on alkalinity measurement by determining bicarbonate directly as Total Inorganic Carbon (TIC).

Sources of error should be sought where an **ionic imbalance of greater than ±15% is obtained for a leachate or leachate contaminated water sample**.

### A13.5.3 Internal checks – analyte ratios

Comparison of electrical conductivity with dissolved ion concentrations The electrical conductivity of a solution is dependent mainly on the concentration and less so on the types of ions present in the solution. Thus:

EC (µS/cm) = k x (total cations in meq 1-1)

or

EC (µS/cm) = k x (total anions in meq 1-1)

where k is a constant ranging from 90 to 125 depending on the average conductance of the ions present.

In relatively unpolluted groundwaters k can be taken as 100. The presence of a high proportion of chloride ions will tend to result in higher k values. In strong solutions (EC > 2000 µS/cm), k will be lower.

**Comparison of electrical conductivity with total dissolved solids**

If Total Dissolved Solids (TDS) has been determined experimentally, the reported value can be compared with a value calculated from the sum of individual ion concentrations (the value should be the same within a reasonable margin of error).

Using the same logic applied above, the electrical conductivity of a solution can be related to total dissolved solids using the relationship:

(TDS in mg/l) = C x (EC in µS/cm)

where C is a constant ranging from 0.54 to 0.96 depending on the average conductance of the ions present.

**Empirical analyte ratios**

Other empirical checks may be derived from experience of a particular monitoring environment. For example, in biodegradable landfill leachate and leachate contaminated groundwaters the following ratio ranges can be used:

* COD/BOD generally falls between 1 and 40.
* COD/TOC generally falls between 2 and 4 and
* TOC/BOD generally falls between 0.5 and 10.

Empirical checks such as these may be used to highlight data for rechecking but should never be used on their own to justify exclusion of data.

### A13.5.4 Internal checks – scope and scheduling

It should be borne in mind that the chemical checks described above provide validation of the major ion chemistry of a sample, and a general check on quality, but provide little direct validation of trace constituent results, many of which are important in assessing contamination risks.

Wherever possible, an agreement should be made with the laboratory to carry out the chemical checks, and criteria set for repeat analyses when checks fail.

### A13.5.5 External checks

**Laboratory QA/QC data**

Evidence of satisfactory compliance with laboratory QA criteria should be obtained and checked. In the case of routine inorganic analyses a simple statement of compliance may suffice. For non-routine and trace organic determinations, a QA report should be supplied with the analysis results. Apparent discrepancies, such as contamination of blank samples with solvents, should be referred to the laboratory.

**Results of QC sampling**

QC sampling results should be separated according to type and each set referenced to the monitoring data to which it applies. Thus, a trip blank will refer to all data from one trip, while a field blank will refer to data from one sampling locality or monitoring protocol. A field standard will generally refer to a single analyte.

Once collated, QC sampling results must be analysed to determine errors and compare these to tolerable uncertainty. The preferred method is to use a control chart (or automated equivalent) for each QC sample set, with action limits set on the basis of data from the initial characterisation monitoring period.

The errors determined from interpretation of QC results should be compared with the tolerable uncertainty associated with each determinand, in order to decide whether the analysis result is acceptable, suspect, or disqualified.

**Sample history reports (field notes)**

Sample history reports should be checked for evidence of unusual conditions or deviations from sampling or handling protocols (e.g. borehole ran dry before purging completed, delayed delivery to laboratory). Analyses susceptible to these conditions should be checked.

**Equipment calibration checks**

Calibration records for equipment used for field measurements should be checked against standardised criteria which will classify the field data as reliable or unreliable. Where calibration records are not available at a suitable frequency, reliability is called into question (particularly applies to pH meters which must be frequently calibrated).

**Laboratory and field measurement comparisons**

Provided field data is quality assured, this comparison can provide information on changes in the sample between collection and analysis. The following measurements are typically made both in the field and laboratory:

* Temperature. Only the field record is representative of the water body. Laboratory temperature indicates sample condition at the laboratory at the time of measurement. A max/min thermometer transported with the sample can be used for sensitive samples.
* pH. A change of 0.5 pH units or more may indicate a change in sample conditions (e.g. degassing of carbon dioxide, precipitation of carbonates, or oxidation reactions). This comparison is obviously not relevant for samples preserved with acid in the field or laboratory.
* Electrical conductivity. change greater than 10% may indicate dissolution of suspended solids (increased EC), or precipitation of solids (decreased EC) and
* Alkalinity. change greater than 10% may indicate a change in sample conditions (e.g. degassing of carbon dioxide, precipitation of carbonates, or oxidation reactions). Not relevant for acid preserved samples.

**Comparison of data between related monitoring points**

‘Related’ monitoring points are monitoring points in the same system (cell, subcatchment, or aquifer) which have been shown to behave similarly (by comparison of historical data). If measurements in the two monitoring points fail to follow historical correlation on a single occasion, the cause should be investigated.

**Comparison of historical data for the same monitoring point**

This check involves preparation of a time series plot, normally prepared as part of data review, but is also a useful validation check. A measurement which deviates from an established trend should be investigated, particularly if other measurements in the same analysis conform to the established trend.

## A13.6 Validation of biological data

The validation of biological monitoring data relies strongly on the confirmation of use of appropriate and consistent methodologies. Careful records must therefore be kept of field and laboratory procedures used, and any deviations from standard practice. This information should be reviewed as part of data validation.

The basic checks for correct monitoring point identification, missing data and transcription errors should be carried out. Similarly, data should be compared to historical and spatial trends to check for inconsistencies. However, because of the number of factors affecting species populations, apparently inconsistent data cannot be discounted without corroborating evidence such as recorded problems with the sampling procedure.

Quality control sampling for macrobiological analysis is generally limited to the use of sampling duplicates, and even these may give more of an indication of natural variability rather than errors. Microbiological analysis should include the use of blanks, standards and spiked samples, and this data will require analysis in a manner similar to chemical QC sampling data.

## A13.7 Automation of data validation

A number of the checks described above may be automated in a computerised data management system, by the use of validation rules (For example, restricting data values to valid ranges, or making certain fields mandatory). Validation rules should be carefully written to avoid rejection of data, which, although abnormal, is valid.

The use of automated validation rules cannot cover all the requirements of data validation. Certain checks (particularly the comparisons with historical data and with data from nearby monitoring points) require professional judgement. Furthermore, all validation rule breaches and suspect data will require follow-up action which is again a matter for professional judgement.

## References

Blakey, N.C., Bradshaw, K., and Lewin, K. (1998). *Leachate monitoring for the Brogborough test cell project*. Environment Agency. Report No. EPG 1/7/13.

Department of the Environment (DoE) (1989). *Guidance on safeguarding the quality of public water supplies*. HMSO. London.

Kehew, A.E. and Passero, R.N. (1990). *pH and redox buffering mechanisms in a glacial drift aquifer contaminated by landfill leachate*. Ground Water, 28, 5, 728-737.

Standing Committee of Analysts (1981). *The determination of alkalinity and acidity in water. Methods for the examination of waters and associated materials*. HMSO. UK ISBN: 0 11 751601 5.

# Glossary

This glossary defines terms as they are used in this document. Some terms may have broader meanings outside this guidance. Within definitions, words in italics are themselves defined elsewhere in the glossary.

#### Acceptable release rate / acceptable leakage rate

A designed leakage rate for leachate egress through an engineered landfill lining system based on a quantitative assessment of risk.

#### Accuracy

The closeness of the result of a measurement to the true value.

#### Acetogenic / acetogenic phase

The initial period during the decomposition of refuse in a landfill, when the conversion of organic polymers, such as cellulose, to simple compounds, such as acetic and other short-chain fatty acids, dominates and little or no methanogenic activity takes place.

#### Analyte

A specific compound or element of interest undergoing chemical analysis.

#### Annulus

The ring-shaped space in a borehole between the borehole lining and the borehole wall.

#### Annular seal

A seal occupying the annulus to prevent vertical movement of water.

#### Appropriate sample

A sample collected and analysed using standard protocols, which is fit for its purpose.

#### Aquifer

A permeable geological stratum or formation that is capable of both storing and transmitting water. A confined aquifer is where an upper layer of low permeability confines groundwater in the aquifer under greater than atmospheric pressure. An unconfined aquifer is where the upper surface of a saturated zone forms a water table within the water-bearing stratum. See Groundwater system.

Aquitard

A geologic stratum or formation of low permeability that impedes the flow of water between two aquifers.

Assessment

The process of evaluating the significance of a departure from baseline conditions by reference to an adverse trend in data or the breach of a specified limit.

Assessment criterion

A test of the significance of a deviation from baseline conditions, which if breached would trigger a series of pre-planned actions.

Assessment limit

A predetermined ‘early warning’ limit value of a measurement, used in some assessment criteria.

Assessment monitoring

An investigative monitoring programme initiated in response to anomalous data or as an action following breach of an assessment criterion.

Attenuation

A decrease in contaminant concentration or flux through biological, chemical and physical processes, individually or in combination (e.g.

dilution, adsorption, precipitation, ion exchange, biodegradation, oxidation, reduction). See also “natural attenuation”.

Background

See “baseline”

Baseline

Measurements that characterise physical, chemical or other distinctive

properties of groundwater and surface water unaffected by leachate contamination.

Baseline or background concentration / level

The value and variability of a measurement in the absence of a landfill.

Bias

The tendency of sampling measurements to be consistently reported to one side of the true result. A systematic error due to the sampling and/or analytical process.

Blank sample

A laboratory prepared sample of reagent-grade water or pure solvent that is used as a quality control sample. See also field blank.

Borehole

A hole sunk into the ground by drilling for abstraction of water or leachate or for observation purposes. A borehole may be lined with suitable casing and screened at appropriate depths.

Borehole development

The process of cleaning out a borehole following its construction in order to remove fine material within and immediately around the screened section of the borehole.

Construction quality assurance (CQA)

A certifiable management system that provides assurance that construction works are completed as specified. See “quality assurance”.

Catchment

The area from which water drains to a specified point (e.g. to a reservoir, river, lake, borehole). See also “landfill catchment”.

Catchment drawing

See “landfill catchment drawing”.

Characterisation monitoring

Monitoring using a broad range of measurements to characterise a water by recording as many measurable properties (e.g. physical, chemical, biological) as practicable.

Compliance

The process of achieving, and the achievement of, conformity with a regulatory standard.

Compliance limit

A regulatory limit established in the regulatory permit, such as a EASR permit or discharge consent.

Composite sample

A sample taken over a range of locations or time intervals. For example,s a sample taken over an extended depth range in a borehole or surface water, or a sample formed by combining a number of discrete samples. Synonymous with “integrated sample”.

Conceptual model

A simplified representation or working description of how the real (hydrogeological) system is believed to behave based on qualitative analysis of field data. A quantitative conceptual model includes preliminary calculations for the key processes.

Conduit flow

Groundwater flow in formations in which flow is almost entirely channelled through discrete solution channels or discontinuities.

Consented discharge

A discharge of effluent controlled by a discharge consent or groundwater authorisation issued by the Agency.

Conservative contaminants

Contaminants which can move readily through the environment with little reaction or degradation (e.g. chloride).

Contamination / contaminant

The introduction of any substance to water at a concentration exceeding the baseline concentration. A contaminant is any such

substance.

Contingency action

A predetermined plan of action to respond to a breach of an

assessment criterion.

Continuous sample

A sample taken continuously over an extended period of time.

Control chart

A graphical statistical method for evaluating changes in monitoring

data.

Cusum Chart

A type of control chart that exaggerates small permanent shifts from

a baseline mean value.

Design leakage

See “acceptable release rate”.

Detection limit

The lowest concentration of a substance that can be reliably measured

to be different from zero concentration.

Determinand

The subject of any measurement or analysis.

Development

See “borehole development”

Diffusion

Migration of dissolved substances within a fluid due to random

movement of particles. Significant when flows are low.

Dilution

Reduction in concentration brought about by the addition of water.

Discharge

A release of leachate or water into another water body.

Discrete sample

A sample taken from a single point in space and time (sometimes known as a “spot sample”).

Dispersion

Groundwater - Irregular spreading of solutes due to heterogeneities in

groundwater systems at pore-grain scale (microscopic dispersion) or at field scale (macroscopic dispersion).

Surface water - spreading of substances through the receiving water by means of differential flow rates and turbulence.

Down-gradient

In the direction of decreasing water level (i.e. in groundwater this is following the hydraulic gradient).

Duplicate sample

A second sample prepared in the same way as a primary sample.

There are several types of duplicate sample (see Appendix 12). See also sampling duplicate.

Effective porosity

The amount of interconnected pore space, through which fluids can pass, expressed as a percent of bulk volume.

Effective rainfall

Total rainfall minus actual losses due to evaporation and

transpiration. Effective rainfall includes both surface run-off and that which percolates into the ground below the soil zone.

Effluent

A waste fluid discharged or emitted to the external environment.

Environmental Authorisations Regulations (EASR)

Refers to the provisions of the Environmental Authorisations (Scotland) Regulations 2018 (EASR).

Environmental quality standard (EQS)

A water quality and biological standard for a surface watercourse.

Error

The total error is the difference between an experimental result and

the “true” value at the time of sampling. The total error is made up of a combination of systematic and random errors resulting from the sampling and measurement process.

Evaporation

The process by which water passes from a liquid to a vapour.

Evapo-transpiration

The total water transferred to the atmosphere by evaporation from the soil or water surface, and transpiration by plants.

Example schedules

Tables of monitoring measurements and sample frequency illustrative of monitoring needs for a landfill in a particular setting. Provided as a model against which site-specific schedules can be compared.

Field blank / standard

A blank or standard sample prepared in the laboratory and taken to the sampling site, from where it is treated in exactly the same way as the sample. Used to detect combined errors in sampling and analysis.

Fissure flow

Groundwater flow in rock or clay formations in which water movement is primarily through fissures.

Fit for purpose

(Describing a process or measurement). Yielding a result that is within the tolerable uncertainty.

Geological formation

An assemblage of rocks which have some characteristics in common, whether of origin, age or composition. Normally now used to refer to an identifiable rock unit within a particular area.

Groundwater

In this document the definition used is that given in the EC Groundwater Directive (80/68/EEC) as “all water which is below the surface of the ground in the saturation zone and in direct contact with the ground or subsoil”.

Groundwater system

A saturated groundwater bearing formation, or group of formations, which form a hydraulically continuous unit.

Hazard

A property or situation that in particular circumstances could lead to harm.

HDPE

High density polyethylene - a plastic material.

Head (hydraulic head)

The sum of the elevation head, the pressure head, and the velocity head at a given point in a water system. In practical terms, this is the height of the surface of a column of water above a specified datum elevation.

Hydraulic conductivity

A coefficient of proportionality describing the rate at which a fluid can move through a medium. The density and kinematic viscosity of the fluid affect the hydraulic conductivity, so that this parameter is dependent on the fluid as well as the medium. Hydraulic conductivity is an expression of the rate of flow of a given fluid through a unit area and thickness of medium, under a unit differential pressure at a given temperature (See also “permeability”).

Hydraulic gradient

The change in total head (of water) with distance in a given direction. The direction is that which yields a maximum rate of decrease in head.

Hydrogeology

The study of water in rocks.

Hydrology

The study of water at ground surface.

Index / Indices

A multivariate statistic which combines a number of monitoring

measurements to produce a numeric value which can be used to represent variability in measurements.

Indicators

Measurements specified as part of a routine monitoring programme, which are used as indicators of leachate contamination or for compliance purposes.

Inert waste

Wastes that do not undergo any significant physical, chemical or biological transformations.

Infiltration

The entry of water, usually as rain or melted snow, into soil or a landfill.

Initial characterisation monitoring

An initial period of intensive characterisation monitoring carried out to provide sufficient data to define the normal pattern of variation in a broad suite of measurements.

Integrated sample

(Term not used in this guidance). Synonymous with composite sample.

Intergranular flow

Groundwater flow through interconnected pore spaces in a soil or rock formation.

Inorganic

Any substance that is not organic.

Ion

An element or compound that has gained or lost one or more electrons, so that it carries a charge.

Ionic balance

See “major ion balance”.

Landfill catchment / Landfill catchment drawing

A drawing or drawings which encompass the up-gradient groundwater and surface water catchment areas containing the landfill site, and the area down-gradient of the site which could potentially be influenced by leachate discharges from the landfill site.

Leachate

The liquid resulting from percolation of water and liquid waste through solid waste.

Major ion

One of several principle ions which together account for the majority of dissolved ions in a water sample.

Major ion balance

A calculation to show the relative amounts of positive and negatively charged ions reported in laboratory results for a solution. All solutions are neutral, so the sum of positive ions should be equal to the sum of negative ions.

Measurement

See “monitoring measurement”.

Methanogenic/ methanogenic phase

An advanced stage of anaerobic decomposition of refuse, when methane is produced in significant quantities.

Minimum reporting value

The lowest concentration of a substance which is reported in the results of an analysis. It is not necessarily the detection limit.

Mixing depth

The depth of groundwater into which leachate escaping from a landfill site is mixed. Used for dilution calculations.

Monitoring

A continuous or regular periodic check to determine the on-going nature of the potential hazard, emissions, conditions along

environmental pathways and the environmental impacts of landfill operations, to ensure that the landfill is performing according to design (adapted from Waste Management Paper 26, 1986).

The general definition of monitoring includes measurements undertaken for compliance purposes and those undertaken to assess landfill performance.

Monitoring infrastructure

The total of all monitoring points and services used for a monitoring programme.

Monitoring measurement

An individual measurement taken from a single monitoring point on a single occasion.

Monitoring point

An individual point or structure from which unique sets of monitoring measurements can be obtained.

Monitoring programme

A series of similar monitoring tasks with a common function. Section 3.7 outlines the principle monitoring programmes for leachate, groundwater and surface water.

Monitoring Plan

See “site control and monitoring plan”.

Natural attenuation

Natural processes which reduce the concentration of contaminants in groundwater and surface water

Organic (compound)

Any substance containing carbon-carbon bonds, or methane or its derivatives.

Pathway

The route by which contaminants are transported between the source of landfill leachate and a water receptor.

Permeability

A measure of the rate at which a fluid will move through a medium. The permeability of a medium is independent of the properties of the fluid. See also “hydraulic conductivity”.

Piezometer

An instrument for measuring hydraulic pressure. The term is commonly applied to a tube installed to allow water level measurement and sampling from a specific vertical interval (the ‘response zone’). The response zone consists of a porous or short screen (i.e. typically less than 6 m in length), or pressure measuring device, isolated by annular seals.

Pollution

Defined in the Environment Protection Act 1990 Section 29(3) as “pollution of the environment due to the release or escape (into any environmental medium) from :

(a) the land on which controlled waste is treated;

(b) the land on which controlled waste is kept;

(c) the land in or on which controlled waste is deposited; and

(d) fixed plant by means of which controlled waste is treated, kept or disposed of, of substances or articles constituting or resulting from waste and capable (by reason of the quantity or concentrations involved) of causing harm to man or any other living organisms supported by the environment”.

Also defined in EASR Statutory Instrument as “emissions as a result of human activity which may be harmful to human health or the quality of the environment, cause offence to any human senses, result in damage to material property, or impair or interfere with amenities and other legitimate uses of the environment”; and “pollutant” means “any substance, vibration, heat or noise, released as a result of such emission which may have such an effect”.

Also defined in the EC Groundwater Directive (80/68/EC) in relation to groundwater as “the discharge by man, directly or indirectly, of substances or energy into groundwater, the results of which are such as to endanger human health or water supplies, harm living resources and the aquatic ecosystem or interface with other legitimate uses of water”.

Also defined in the EC Water Framework Directive (2000/60/EC) as ‘the direct or indirect introduction, as a result of human activity, of substances or heat into the air, water or land which may be harmful to human health or the quality of aquatic ecosystems or terrestrial ecosystems directly depending on aquatic ecosystems, which result in damage to material property, or which impair or interfere with amenities and other legitimate uses of the environment.

Precision

The repeatability of a measurement. The closeness of each of a

number of similar measurements to their arithmetic mean.

Protocol

A standardised procedure for carrying out a monitoring task, such as

sampling, handling, analysis, or data management. (Use of a protocol can help to ensure consistency and repeatability).

Purging

The process of removing water which is unrepresentative of the

surrounding strata or waste from a borehole, prior to sampling.

Quality assurance (QA)

A management function, involving all those planned and systematic actions necessary to provide adequate confidence that a product or service will satisfy given requirements for quality.

Quality control (QC)

The operational techniques and activities that are used to fulfil requirements for quality. Includes methods for minimising errors (such as use of appropriate protocols) and methods for detecting errors (such as check measurements, e.g. QC sampling).

QC sampling

The preparation and analysis of samples for the purpose of detecting

errors introduced by the monitoring process. Examples of QC samples include duplicates, blanks, standards, and spiked samples.

Random error

Error due to random variation in the performance of the sampling and measurement process.

Receptor

A groundwater or surface water, amenity or abstraction point.

Recharge

The amount of water added to the groundwater system by natural or

artificial processes.

Remediation

The process of improving the quality of a polluted body of water or

an area of land, either by carrying out works on the pollutant source or by treatment of the affected water or land.

Representative sample

An ideal water sample that retains the chemical and physical

characteristics of the in-situ water.

Resistivity

The electrical resistance offered to the passage of a current, usually expressed in ohm-metres. The reciprocal of conductivity.

Resistivity array

A permanently installed grid of electrodes used to measure resistivity on a periodic basis as a means of monitoring changes in the electrical properties of strata.

Risk

A quantitative or qualitative combination of the probability of a defined hazard causing an adverse consequence at a receptor, and the magnitude of that consequence.

Risk assessment

The process of identifying and quantifying a risk, and assessing the significance of that risk in relation to other risks.

Risk-based monitoring assessment

A document using the results of site investigation and risk assessment to rationalise monitoring priorities for a landfill.

Risk inventory

A tabular summary of risk to receptors from a landfill for the purpose of prioritising monitoring effort.

Routine monitoring

Monitoring that is undertaken once initial characterisation monitoring has been completed, and consisting of ongoing characterisation, together with indicator measurements. Routine monitoring continues until an impact is detected (leading to assessment monitoring) or completion monitoring is implemented.

Run-off

Rain or melted snow that drains from the land surface.

Sampling duplicate

A sample taken immediately following another sample by repeating the entire sampling procedure. Both samples are then treated identically. Used to determine total random errors in the entire sampling and analysis process.

Sampling protocol

A protocol for carrying out a specific sampling task.

Saturated zone (phreatic zone)

The zone in which the voids of the rock or soil are filled with water at a pressure greater than atmospheric. The water table is the top of the saturated zone in an unconfined groundwater system. In general, flow on a macro scale is horizontal and typically faster than for unsaturated zone flow. Flow rates between different types of strata vary over several orders of magnitude.

Significant deviation

The amount of deviation from the norm that would give cause for concern.

Site control and monitoring plan

A reference document detailing the operation, design, management and implementation of a monitoring scheme for a landfill.

Spiked sample

A water sample to which a known amount of a specific analyte has been added.

#### Spot samples

Groundwater – a sample taken from a specific depth in a borehole.

Surface water – a sample taken almost instantaneously from a specific location in a surface water, or from a discharge.

Synonymous with “discrete sample”.

Stabilisation

In relation to landfill, this is the degradation of organic matter to stable products, and the settlement of fill to its rest level.

Standard sample

A quality control sample in which the concentration of a specific or group of chemical constituents is known. See also field standard.

Surface water

Any accumulation of water on the ground surface including ponds, lakes, wetlands, drains, ditches, springs, seepages, streams and rivers.

Systematic error

Error introduced by the sampling and measurement process that consistently biases the result in one direction.

Time-series

A graphical representation of data arranged sequentially by date.

Tolerable uncertainty

The degree of uncertainty that is acceptable without compromising the purpose of the measurement.

Transpiration

The transfer of water from the soil to atmosphere by plants.

Trigger levels

Concept used to identify deterioration in groundwater quality beyond

which a significant adverse environmental effect has occurred

Turbidity

Cloudiness in water, or other liquid e.g. leachate, due to the presence of suspended and/or colloidal organic and inorganic solid material.

Uncertainty

The interval around the result of a measurement that contains the true value with high probability. Uncertainty is caused by undetected or unpredicted errors in the sampling and measurement process, together with unpredicted natural variation.

Up-gradient

In the direction of increasing hydraulic head (i.e. in groundwater this is moving up the hydraulic gradient).

Unsaturated zone (vadose zone)

The zone between the land surface and the water table. The pore space contains water at less than atmospheric pressure, as well as air and other gases. Saturated bodies, such as perched groundwater may exist in the unsaturated zone. Also called the vadose zone.

Overall flow, on a macro scale, is downward (gravity driven); moisture content is low and water normally flows slowly in close contact with the rock matrix.

Water balance

An evaluation of all the sources of supply, storage and corresponding discharges of water - For example, within a landfill site or an entire surface water catchment area.

Water body

A continuous mass of water with similar characteristics, which can be represented on a map or plan. For example, groundwater within a specific stratum, water in a lake, water in a stream course.

Water quality objective

A chemical and or biological objective for a body of water such as to be fit for a particular use – e.g. abstraction for potable supply or for target organism such as freshwater fish.

Well

A hole sunk into the ground for abstraction of water or leachate or for observation purposes. A well is generally of larger diameter than a borehole and dug rather than drilled.

**This guidance has been updated to meet accessibility standards and to replace certain references to legislation with references to the Environmental Authorisations (Scotland) Regulations 2018. It has not been reviewed beyond this. We are aware that sections of this guidance may need to be updated, and this work will be completed in due course.**

## Disclaimer

This guidance is based on the law as it stood when the guidance was published.

Whilst every effort has been made to ensure the accuracy of this guidance, SEPA gives no warranty, covenant or undertaking (express or implied) regarding the fitness for purpose of, or any error, omission or discrepancy in this guidance. Reliance on its contents and the contents of any websites that are linked to or from this guidance is entirely at the user’s own risk. SEPA is not liable for any loss or damage that may come from using this guidance. This includes:

* any direct, indirect and consequential losses
* any loss or damage caused by civil wrongs, breach of contract or otherwise.

SEPA reserves the right to depart from this guidance and take appropriate action as it considers necessary or appropriate. Operators are responsible for ensuring that they are compliant with the law. If necessary, independent legal / specialist advice should be sought.

1. Standing Committee of Analysts, 1996. General Principles of Sampling Waters and Associated Materials (2nd edition). [↑](#footnote-ref-1)
2. Cheeseman R.V. and Wilson A.L. (revised, Gardner M.J.), 1989. A Manual on Analytical Quality Control for the Water Industry. Manual NS30. Water Research Centre plc. [↑](#footnote-ref-2)
3. If these variations are understood and characterised, they can be accounted for and their contribution to uncertainty diminishes. [↑](#footnote-ref-3)
4. “Descriptive statistics” refers to a summary of site investigation or other supporting data and may include For example,: the number of samples, minimum, maximum, average, median, standard deviation 95 percentile. [↑](#footnote-ref-4)
5. m.AOD: metres above Ordnance Datum. [↑](#footnote-ref-5)
6. Data can be gathered from weather stations established on the landfill, though longer term statistical or interpretative data is generally more reliably obtained from the Met Office and SEPA. [↑](#footnote-ref-6)
7. i.e. the 95 or 90 percentile low flow value. [↑](#footnote-ref-7)
8. Flow statistics for larger stream courses may be available from the SEPA. [↑](#footnote-ref-8)
9. This would be demonstrated by comparison between monitoring points and the main leachate collection point. [↑](#footnote-ref-9)
10. In some instances (e.g. rotary air flush drilling in fissured strata) a larger distance is necessary. [↑](#footnote-ref-10)
11. Legal rights of access are provided for in Section 35(4) of the Environment Protection Act 1990 as amended by Paragraph 67, Schedule 22 of the Environment Act 1995. [↑](#footnote-ref-11)
12. See previous footnote to Section 6.2.3. [↑](#footnote-ref-12)
13. At least two surface water monitoring points per uniform water body are required. At least three groundwater boreholes per uniform water body are required. [↑](#footnote-ref-13)
14. As provided for under the Control of Substances Hazardous to Health Regulations 1989. [↑](#footnote-ref-14)
15. For example, where it is not possible to place a monitoring point at a sufficient distance downstream of a discharge to allow complete mixing. [↑](#footnote-ref-15)
16. i.e where the screen spans more than one groundwater flow zone, or is longer than 6 metres (see 8.5.1). [↑](#footnote-ref-16)
17. In low ionic strength waters (which will exhibit low electrical conductivity), it may be difficult to obtain a stable pH reading. This problem can be overcome to some extent by using specialist electrodes. [↑](#footnote-ref-17)
18. i.e. when water in the screened length is considered sufficiently representative, and the sonde does not cause excessive disturbance of the water column. [↑](#footnote-ref-18)
19. Where protocols are carried out in parallel (e.g. in the case of SEPA audit monitoring), both should be subject to QC samples, For example, separated duplicate samples (see glossary). [↑](#footnote-ref-19)
20. The approach adopted for ‘non-detects’ should be consistent, and also risk-based. Substitution with zero may be acceptable in low risk situations; however when detection limits are significant in relation to assessment limits, allowance must be made for the range of values which could be represented by the non-detect, and an alternative value such as the LOD or 2/3rds LOD may be appropriate. [↑](#footnote-ref-20)
21. For example, Mazor, 1991, Hem 1975 for graphical presentation of water quality data; Gibbons, 1997 on statistical methods applied to groundwater data. [↑](#footnote-ref-21)
22. i.e. strata of sufficient strength to stand unsupported [↑](#footnote-ref-22)
23. Inductively Coupled Plasma – Atomic Emission Spectroscopy [↑](#footnote-ref-23)
24. Atomic Absorption Spectroscopy [↑](#footnote-ref-24)
25. Inductively Coupled Plasma – Mass Spectroscopy [↑](#footnote-ref-25)
26. Gas Chromatography – Flame Ionisation Detector [↑](#footnote-ref-26)
27. An interlaboratory proficiency testing scheme for water samples [↑](#footnote-ref-27)
28. Laboratory Environmental Analysis Proficiency scheme [↑](#footnote-ref-28)