# Major non-compliance: point source discharges (excluding sewage)

Table 1: Major impact of the authorised activity

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Any authorisation condition. | Non-compliance causes or is likely to cause: - Category 1 or 2 environmental event. - Breach of water standard. - Significant and sustained adverse trend for groundwater. | - Environmental events guidance. - Relevant water standards. - Groundwater monitoring or modelling demonstrates significant and sustained adverse trend. | Demonstration that the cause or likely cause of the harm has ceased or been resolved. This can include monitoring and modelling. |
| Descriptive conditions. No significant: - Iridescence / sheen; - Discolouration; - Deposition of solids; - Increased foaming; or - Microbiological growth; in receiving waters | Non-compliance causes or is likely to cause a Category 1 or 2 environmental event. | - Site inspection. - Environmental events guidance. - Descriptive conditions guidance | Demonstration that the cause or likely cause of the harm has ceased or been resolved, and the visual impact is now compliant. |
| Single-tier numeric limits set to achieve environmental standards. | - More than twice the limit specified in authorisation. - Exceptions: - pH: limit exceeded by more than 1 unit. - Temperature: exceeded by more than 5oC. - Any breach of single tier bacterial limit. | Assess against authorisation limit using: - SEPA monitoring data. - Operator self-monitoring. - Regulatory Method (WAT-RM-40). | - Major non-compliance remains until next compliant sample. - Seasonal sampling – if a discharge is major non-compliant at the end of the season this will be lifted. |
| Two-tier numeric limits set to achieve environmental standards (set according to a specified statistical distribution). | - Any breach of upper-tier limit. - Number of planned samples exceeding lower tier limit is greater than the maximum number of permitted exceedances specified in the look up table. Exception: A breach of the upper tier UWWTD limit where sample compliance is achieved by meeting the minimum percentage reduction of influent load. | Assess against authorisation conditions and permitted exceedances look up table: - SEPA monitoring data. - Operator self-monitoring. - Regulatory Method (WAT-RM-40). | - Upper tier: when the next planned sample result is compliant. - Lower tier: when number of planned samples exceeding lower tier limit is less than the maximum number of permitted exceedances in the previous 12 months - specified in the look up table. - Seasonal sampling – if a discharge is major non-compliant at the end of the season this will be lifted. |
| Annual numerical limits | Any breach of the limit specified in the authorisation. ​Exception: A breach of the annual mean UWWTD limit where sample compliance is achieved by meeting the minimum percentage reduction of influent load. | Assess against limit in authorisation e.g. - Annual mean limits for iron or aluminium in samples taken over a 12-month rolling period. - UWWTD annual mean limits for phosphorus or nitrogen (in composite samples taken over a calendar year), taking into account, where appropriate, percentage reduction in influent loading. Using: - SEPA monitoring data. - Operator monitoring data. - Regulatory Method (WAT-RM-40). | - For limits based on a rolling 12-month period, the major non-compliance will apply from the date of the breach until the point when data from the previous 12 months does not exceed the authorisation limit. - For limits based on a calendar year, major non-compliance will apply from the date of the breach until the end of the relevant calendar year. |

Table 2: Scope of site

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Discharge points specified in the authorisation. | Discharge points not as specified in authorisation and / or Diffuser(s) or outfall location not achieving acceptable dispersion as assessed by visual assessment and/ or investigative monitoring. | - Site inspection - NGR check. - SEPA investigative monitoring data. | Evidence provided that the discharge point is at the authorised location. |
| Storm overflow or emergency overflow settings. | Failure to meet any conditions relating to storm overflows or emergency overflows as specified in the authorisation. | - Data returns. - Site inspection. - Records review. - Operator incident report. | Report provided that identifies the cause, actions taken and demonstrates compliance, this should include spill event data. |
| Screens. | Screens required by authorisation are: - Not installed OR - Maceration of comminution is used to achieve screening standards. | - Site inspection. - Environmental events guidance. Note: If a screen is present but not operating, it should be assessed under Table 4 (management of site). | Evidence provided that screens have been installed and are operating or that maceration / comminution plant has been decommissioned. |
| Treatment system as specified in the authorisation. | Treatment system specified in authorisation is not provided. | - Site inspection. - Environmental event investigation. Note: If the treatment plant (e.g. waste water treatment plant, settlement lagoons, oil interceptor, reed beds) is present but not operating, has frequent breakdowns, not operating as designed, not as per authorisation condition or not operating during critical period, it should be assessed under Table 4 (management of site). | Evidence provided that demonstrates treatment plant is as specified in the authorisation. |
| Authorised medicines and substances used in aquaculture hatcheries. | ​Using medicine or substance at concentrations greater than specified in the authorisation or not administered as specified in the authorisation. | - ​Operator submission reviews. - ​Site inspection. | Discharge has ceased, reduced to within limits or activity is undertaken in line with authorisation. |

Table 3: Understanding of authorised activities

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Requirement to report incidents (either in operation of plant or environmental events). | - Unless specified otherwise in the authorisation, failure to notify SEPA within 24 hours of an event that has caused or could cause an adverse impact upon the environment, human health and wellbeing. - Failure to provide incident report requested by SEPA within 14 days (or agreed date) or the report does not comply with the information requirements specified in the authorisation. | - Operator notification received within timescale – by phone call or email. - Operator incident report submitted in accordance with authorisation conditions. - Assessment of operator incident report and the timescale that it was submitted. - Authorisation provides definition of incident or event. “incident” means any of the following situations: - Accidents, malfunction, breakdown, or failure of plant or techniques. - Or any event such as force majeure or emergency actions, that results or is likely to result, in a breach of any condition of the authorisation. | Notification and / or incident report received with an explanation why there was a failure to comply and what actions will be / have been taken to ensure compliance in the future. |
| Requirement to submit data (records, reports, data). | Failure to make a data return (including nil returns) of adequate quality within 30 days of the required submission date. | - Annual data return assessments (where required by the authorisation). - Other reports required by the authorisation including: - Increase or introduction of hazardous substances (List I or II substances). - Notifications of use of medicines at fish hatcheries as specified in the authorisation. - Data returns. | - Required data submission. - Or if no data available, MNC will be resolved on receipt of an information submission that includes: - Corrective actions and reasons for missing information. - Assessment of the likely impact from missing data. - Evidence that the records are now being recorded and kept. - SEPA will assess submission and ascertain if enough information is provided to resolve compliance. |
| Requirement to keep records. | - Failure to provide upon request information required to be kept by the authorisation. - Information submitted is not true and accurate. - Records are not kept for the minimum duration specified in the authorisation. | - ​Site inspection. - ​Desk-based inspection. - ​Incident investigation. | - Required data submission. - Or if no data available, MNC will be resolved on receipt of an information submission that includes: - Corrective actions and reasons for missing information. - Assessment of the likely impact from missing data. - Evidence that the records are now being recorded and kept. - SEPA will assess submission and ascertain if enough information is provided to resolve compliance. |
| Provision of suitable sampling locations. | Sampling location required by authorisation not provided or failing to provide a representative sample. | Site inspection. | Evidence provided that sample point is installed and / or provision of a representative sample. |

Table 4: Overall management of authorised activities

| Authorisation condition | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Compliance with authorisation conditions. | - Multiple non-compliance (same or different conditions) that cumulatively equate to major non-compliance. - The major non-compliance will be recorded against the condition that places the responsibility on the Authorised Person to ensure compliance with the conditions of the authorisation. | Having regard to condition-specific guidance where this exists and / or environmental events guidance and events records. - Greater than or equal to four category 3 events within a 365-day period that have been caused by a breach of the same condition. - Unless otherwise stated within the site authorisation, multiple non-compliance breaches may be considered collectively as major non-compliance depending on the particular circumstances. SEPA's assessment will be subject to additional governance checks to ensure national consistency in decision-making. | ​Demonstration that the cause or likely cause of the harm has ceased or been resolved. This can include monitoring and modelling. |
| Operation and calibration of measuring and monitoring equipment required by authorisation (flow meters, event records, autosamplers, telemetry). | - Monitoring equipment not present or not calibrated in line with manufacturers guidance for extended periods of time, for example: - Breakdowns of inlet flow meter(s) exceed 108 days in 12 months. - Breakdowns of event recorders and flow meters at overflows exceed 30 days in 12 months. - No calibration checks of flow meters and/or event recorders performed in accordance with authorisation requirements. - Required telemetry is not operating. - Final effluent autosamplers are not operating according to the authorisation conditions e.g. not at correct temperature. | - Assessment of data returns. - Site inspection. - SEPA request for data and calibration records. - Incident notifications. Calibration of flow meters, use guidance document on calibration of monitoring and measuring equipment as a guide (CAS-G-002). | Evidence provided that the equipment issues resolved and is operating as it should – including evidence of calibration checks where appropriate. |
| Conditions covering management of site, activity infrastructure, equipment. | - Plant / infrastructure: - Frequent breakdown of critical plant with minor unauthorised releases. OR - Infrequent or frequent breakdown of any plant (critical* and non-critical) that leads to, or may lead to, a significant breach of numeric limits (verified by investigative not routine sampling). - No surface water drainage system provided for construction water run-off. | - Assessment of data returns. - Site inspection. - Notification of incidents. - SEPA investigative monitoring data. “critical plant” is defined as those parts of a treatment system that have a significant and immediate role in ensuring discharge effluent quality standards and whose failure is difficult to mitigate without there being a significant effect on effluent quality. Note: this will cover infrastructure required by condition in the authorisation for example treatment plants, settlement lagoons, oil interceptors, screens, disinfection, alarms (not an exhaustive list). | - Evidence provided that the equipment issues resolved and is operating as it should. - SUDS provided for construction water run-off and operating as it should. |
| Management plans or other plans as specified in authorisation. | No plans available. | - Management plans or other plans specified in authorisation such as: - effluent sampling plan. - permitted substances working plan. - sludge handling method statement not available upon request. | - When an acceptable management plan is submitted. - SEPA will assess submission and ascertain if enough information is provided. |

Table 5: Wider legal environmental requirements and financial non-compliance

EPAS is designed to provide a more accurate picture of legal environmental compliance. Under EPAS we will therefore assess compliance of the following situations as it is important a performance rating reflects this.

| Contravention | Major non-compliance | How will SEPA assess / supporting guidance | Return to compliance examples |
| --- | --- | --- | --- |
| Undertaking a regulated activity without authorisation. | Undertaking a regulated activity without authorisation, for example: - Use of chlorination to achieve disinfection, contrary to authorisation condition. - Chemical dosing to achieve discharge standards. | Site inspection. | Unauthorised activity ceases, and, where appropriate, authorisation is varied to include the activity or appropriate authorisation obtained. |
| Environmental event at an authorised site that is unrelated to the authorised activity. | Causes a: - Category 1 or 2 environmental event. - Breach of water or air quality standard. - Significant and sustained adverse trend for groundwater. Example: oil spill. | - Environmental events guidance. - Groundwater monitoring, investigation or modelling demonstrates significant and sustained adverse trend. | Demonstration that the cause or likely cause of the harm has ceased or been resolved. This can include monitoring and modelling. |
| Non-payment of annual charges. | Escalation to debt collection or if debt goes into the next financial year. (Non-compliance is when payment is more than 90 days late.) | - Monthly debtors report. | Payment of annual charges. (Payment plan agreed with SEPA is equivalent to a compliance recovery plan.). |

<Report date here (month, year)>

For information on accessing this document in an alternative format or language, please contact SEPA by email or telephone 0300 099 6699.

If you are a user of British Sign Language (BSL), the Contact Scotland BSL service gives you access to an online interpreter, enabling you to communicate with us using sign language.

Adequate quality means containing the required information to enable the assessment of compliance with authorisation conditions.